- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I», unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ASTM B283, Standard Specification for Copper and Copper-Alloy Die Forgings (Hot-Pressed).

      - MSS-SP-80, Bronze Gate, Globe, Angle and Check Valves.

      - MSS-SP-85, Cast Iron Globe and Angle Valves, Flanged and Threaded Ends.

  - Submittals

    - Product Data:

      - Submit shop drawings and technical data in conformance with client’s instructions.

      - Submit characteristic curves of balancing valve for verification.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, series or model reference number;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

  - Manual Balancing Valve

    - Globe Valve.

      - General

        - Globe valve inclined “Y” body, designed to allow pressure measurements and to ensure a precise regulation of flow. Pressure tapings are located at the inlet and exit of the valve to receive a differential pressure gauge.

        - Precision: The measured and displayed flow is within 25% of actual flow.

      - Diameters less than or equal to DN 2.

        - Dezincification resistant brass body, solder or sweat end connections, EPDM seat ring and dezincification resistant brass plug, and screw in bonnet, which can withstand a maximum working pressure of 1.7 MPa (250 psi) and a maximum service temperature of 121C (250F).

        - Flow regulation: Minimum 4 complete turns of the handwheel with visual dial indicator and built-in memory stopper.

      - Diameters equal or greater than DN 2 ½.

        - Epoxy coated cast iron body; all wetted brass parts shall be alloyed to resist dezincification. Grooved to 300lbs or flanged to 125lbs ANSI standard connections which can withstand a maximum working pressure of 1.7 MPa (250 psi) and a maximum service temperature of 121C (250F).

        - Flow regulation: Minimum 8 complete turns of the handwheel with visual dial indicator and built-in memory stopper.

      - Acceptable component:

        - Globe Valve: Flo Fab series LGS or LGSS.

        - Grooved Globe Valve: Flo Fab series LGSG.

    - Ball Valves.

      - Flow regulation by straight handle with flow lock memory stopper.

      - Differential pressure measurement taken across a venturi throat, accuracy of ±3%.

      - Diameters less than or equal to DN 2: Forged bronze body ASTM-B283, teflon seats and packing, threaded connections, maximum working pressure 1.7 MPa (250 psi) and maximum service temperature 121C (250F).

      - Acceptable component: Flo Fab series LASN.

      - Diameters equal or greater than DN 2 ½: carbon steel body SA-53, teflon seats and packing, interior flow straightening vanes, flanged, grooved, or solder connection which can withstand a maximum working pressure of 1.7 MPa (250 psi) and a maximum service temperature of 121C (250F).

      - Acceptable component: Flo Fab series LASN, LAF, LAG, and LAW.

    - Pressure Ports.

      - DN 3/4 Schrader type ports allow hose connection. Capped when not in use or hosing can be permanently attached for continuous pressure readings.

  - Flow Control & Combination Ball Valve.

    - Valves designed to automatically maintain a fixed flow despite pressure fluctuations.

      - Operation: the pre-calibrated orifices close when the pressure difference increases and open if the pressure difference decreases.

      - Valves are factory pre-calibrated. Forged Brass body ASTM B283, 600 WOG EPDM/viton O-rings, stainless steel/brass flow cartridge, operational with a differential pressure [7 to 110 kPa (1 to 15 psi)] [14 to 220 kPa (2 to 30 psi) ] [28 to 440 kPa (4 to 60 psi)].

      - Maximum working pressure: 4.13 MPa (600 psi).

      - Maximum service temperature: 190°C (375°F).

      - Flow rates as indicated in the plans and specifications.

      - Acceptable component: Flo Fab series UM.

- PART 3 – EXECUTION

  - Balancing

    - Install balancing valves where indicated.

    - Balance water system so that the actual throughput is 90% of the calculated.

    - Use the balancing methods described in "Testing, adjusting and balancing systems”.

  - Cleaning and rinsing

    - Comply with section describing “Cleaning and disinfection of pipes, fittings and components”.

End of Section