- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I», unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ASTM B283, Standard Specification for Copper and Copper-Alloy Die Forgings (Hot-Pressed).

      - MSS-SP-80, Bronze Gate, Globe, Angle and Check Valves.

      - MSS-SP-85, Cast Iron Globe and Angle Valves, Flanged and Threaded Ends.

  - Submittals

    - Product Data:

      - Submit shop drawings and technical data in conformance with client’s instructions.

      - Submit characteristic curves of balancing valve for verification.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, series or model reference number;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

- Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model  LGS or FODRV or comparable product by the following:

    - Manual Bronze Calibrated-Orifice Balancing Valve

- Body: Bronze, ball or plug type with calibrated orifice or venturi.

- Ball: Brass or stainless steel.

- Plug: Resin.

- Seat: PTFE.

- End Connections: Threaded or socket.

- Pressure Gage Connections: Integral seals for portable differential pressure meter.

- Handle Style: Lever, with memory stop to retain set position.

- CWP Rating: Minimum 300 psig (2069 kPa).

- Maximum Operating Temperature: 250 deg F (121 deg C).

Flow rates as indicated in the plans and specifications.

    - Manual Bronze Calibrated-Orifice Balancing Valve

- Cast-Iron or Ductile Iron, Calibrated-Orifice, Balancing Valves:

- Body: Ductile iron, ball, plug, or globe pattern with calibrated orifice or venturi.

- Ball: Brass or stainless steel.

- Stem Seals: EPDM O-rings.

- Disc: Glass and carbon-filled PTFE.

- Seat: PTFE.

- End Connections: Flanged or grooved.

- Pressure Gage Connections: Integral seals for portable differential pressure meter.

- Handle Style: Lever, with memory stop to retain set position.

- CWP Rating: Minimum 300 psig (2069 kPa).

- Maximum Operating Temperature: 250 deg F (121 deg C)

Flow rates as indicated in the plans and specifications.

- .

- Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model  LASN comparable product by the following:

      - Flow regulation by straight handle with flow lock memory stopper.

      - Differential pressure measurement taken across a venturi throat, accuracy of ±3%.

      - Diameters less than or equal to DN 2: Forged bronze body ASTM-B283, teflon seats and packing, threaded connections, maximum working pressure 1.7 MPa (250 psi) and maximum service temperature 121C (250F).

      - Diameters equal or greater than DN 2 ½: carbon steel body SA-53, teflon seats and packing, interior flow straightening vanes, flanged, grooved, or solder connection which can withstand a maximum working pressure of 1.7 MPa (250 psi) and a maximum service temperature of 121C (250F).

    - Pressure Ports.

      - DN 3/4 Schrader type ports allow hose connection. Capped when not in use or hosing can be permanently attached for continuous pressure readings.

      - Flow rates as indicated in the plans and specifications.

- Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model  UM comparable product by the following:

  - Automatic Flow Control & Combination Ball Valve.

    - Valves designed to automatically maintain a fixed flow despite pressure fluctuations.

      - Operation: the pre-calibrated orifices close when the pressure difference increases and open if the pressure difference decreases.

      - Valves are factory pre-calibrated. Forged Brass body ASTM B283, 600 WOG EPDM/viton O-rings, stainless steel/brass flow cartridge, operational with a differential pressure [7 to 110 kPa (1 to 15 psi)] [14 to 220 kPa (2 to 30 psi) ] [28 to 440 kPa (4 to 60 psi)].

      - Maximum working pressure: 4.13 MPa (600 psi).

      - Maximum service temperature: 190°C (375°F).

      - Flow rates as indicated in the plans and specifications.

- PART 3 – EXECUTION

  - Balancing

    - Install balancing valves where indicated.

    - Balance water system so that the actual throughput is 90% of the calculated.

    - Use the balancing methods described in "Testing, adjusting and balancing systems”.

  - Cleaning and rinsing

    - Comply with section describing “Cleaning and disinfection of pipes, fittings and components”.

End of Section