- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I», unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Buttwelding Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

  - Submittals

    - Submit shop drawings and technical data in conformance with client’s instructions.

    - Submit characteristic curves of multi-function valve for verification.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, series or model reference number;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCTS

  - MultiFunction Valve

    - Provide and install valves function straight triple accordance with the plans and in accordance with the following specification:

      - The valves are designed to combine the following three functions:

        - Isolation Valve;

        - Check Valve;

        - Balancing Valve.

    - Epoxy coated cast iron valve body with grooved to 150lbs or flanged to 125lbs ANSI end connections which can withstand a maximum working pressure of 1034 kPa (150 psi) and maximum operating temperature up to 108°C (225°F).

    - Valve include a replaceable bronze disk with EPDM gasket that mates onto a bronze seat, a stainless steel rod and spring that provides constant pressure to prevent against vibration.

    - Pressure tapings are located at the inlet and exit of the valve to receive a differential pressure gauge.

    - Flow rates as indicated in the plans and specifications.

    - Acceptable component: Flo Fab series MFV.

- PART 3 – EXECUTION

  - Installation

    - Install multi-function valve where indicated.

    - The multi-function valve is to be mounted so that the fluid flows in the direction as indicated by the embossed arrow on the valve body.

    - Balance water system so that the actual throughput is 90% of the calculated.

    - Use the balancing methods described in "Testing, adjusting and balancing systems”.

End of Section