- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I», unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Buttwelding Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel Structures.

  - Submittals

    - Product Data:

      - Submit shop drawings and technical data in conformance with client’s instructions

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, series or model reference number;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

- Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model  ASDFF comparable product by the following:

  - Suction Diffuser

    - Angle [cast iron] [ductile]-iron body and end cap, pump-inlet fitting, Maximum working pressure [175-psig (1204-kPa)] [300-psig (2060-kPa)] and maximum working temperature 121C (250F).

    - Connection: Flanged Rating Class 125 ANSI flat face.

    - Suction Diffuser is a combination flow straightener and strainer. Strainer portion is composed of a “Start-up” mesh and permanent cylindrical sieve.

      - “Start-Up” strtainer Sieve: 20 screen mesh.

      - Permanent Strainer Sieve: Stainless Steel cylinder perforated with 3/16" (4.76 mm) holes.

    - All suction diffusers are designed to withstand a differential pressure equal to the maximum head of the pumping system at no flow.

    - The length of the flow straightening vanes will not be less than twice the diameter opening of the discharge flange connection.

    - Flow and size: according to the pump tables on [piping schematics] [specifications].

    - Drain Plug

    - Adjustable foot mounted support.

- PART 3 – EXECUTION

  - Installation

    - Installation shall conform to National Plumbing Code of Canada and any other local laws and regulations.

    - Install strainers allowing sufficient space to perform regular removal and maintanence of the screen and is correctly oriented, arrow embossed on body indictes direction of flow.

    - Install foot support or pipe hangers such that the pump flange is not supporting the weight of upstream fittings and piping. Refer to details and installation instructions of the manufacturer.

    - Start-up:

        - Ensure that the screen is easily accessible;

        - Do not proceed with the start-up unless all of the deficiencies have been identified and corrected;

        - Start-Up sieve with attached contaminates is to be removed and discarded after the initial start-up sequence.

End of Section