- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I», unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B40.1, Pressure Gauges and Gauge attachments.

  - Submittals

    - Product Data:

      - Submit shop drawings and technical data in conformance with client’s instructions.

    - Identify the features listed on the manufacturer's documentation:

      - Pressure gage;

      - Pressure snubber;

      - Isolation valves;

      - Siphons.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, series or model reference number;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

  - Pressure Gage

    - Dial indicator type with 4-1/2" (114 mm) diameter dial face.  Conforming to ANSI / ASME B40.1, Class 2A, accurate to within 1%, unless otherwise indicated.

      - Gage housing and ring is constructed of polished stainless steel.  Internal working mechanism constructed of stainless steel. Gage can be recalibrated.

      - Choose gauges with the consideration of the range and graduation of pressures to be measured, ensuring that the nominal pressure is close as possible to the center of this range.

      - Acceptable component: Flo Fab DRY series RFF0400D5 and Flo Fab LIQUID FILLED series RFF0400LF.

    - Each gage must have an isolation ball valve installed at the inlet of the gage.

      - Glycerin filled gages are to be used at the pump suction and discharge as well as in areas where there is excessive pulsations.

      - Install an isolation siphon when used on steam networks.

      - Install a diaphragm connector when used on a corrosive fluid network.

- PART 3 – EXECUTION

  - Installation

    - Install pressure gages at these recommended locations:

      - At the suction and discharge of pumps;

      - Upstream and downstream of pressure reducing components;

      - Upstream and downstream of pressure regulating valves;

      - All  entrances and exits of heat exchangers and boiler systems;

      - All other indicated location.

    - Use extension piping when the gauges are mounted on insulated piping.

    - Supply and pre-install fittings for gauges where proper system balancing will require pressure measurements.

End of Section