- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I», unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B40.1, Pressure Gauges and Gauge attachments.

  - Submittals

    - Product Data:

      - Submit shop drawings and technical data in conformance with client’s instructions.

    - Identify the features listed on the manufacturer's documentation:

      - Pressure gage;

      - Pressure snubber;

      - Isolation valves;

      - Siphons.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, series or model reference number;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

  - Metal-Case Industrial-Style, Dial-Type Pressure Gage

- Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model  FFBR or FFBRLF comparable product by the following:

          - Standard: ASME B40.100.

          - Case: [Liquid-filled] [Sealed] [Open-front, pressure relief] [Solid-front, pressure relief] <Insert type> type(s); [cast aluminum or drawn steel] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter.

          - Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

          - Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

          - Movement: Mechanical, with link to pressure element and connection to pointer.

          - Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

          - Pointer: Dark-colored metal.

          - Window: [Glass] [or] [plastic] <Insert material>.

          - Ring: [Metal] [Brass] [Stainless steel].

          - Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

- PART 3 – EXECUTION

  - Installation

    - Install pressure gages at these recommended locations:

      - At the suction and discharge of pumps;

      - Upstream and downstream of pressure reducing components;

      - Upstream and downstream of pressure regulating valves;

      - All  entrances and exits of heat exchangers and boiler systems;

      - All other indicated location.

    - Use extension piping when the gauges are mounted on insulated piping.

    - Supply and pre-install fittings for gauges where proper system balancing will require pressure measurements.

End of Section