- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / API 609, Lug and Wafer Type Butterfly Valves.

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

      - ANSI / ASME B16.22, Wrought Copper and Copper-Alloy Solder Joint Pressure Fittings.

      - ANSI / ASME B16.25, Butt welding Ends.

      - ANSI / ASME B16.34, Valves – Flanged, Threaded and Welding Ends.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / ASME B40.1, Pressure Gauges and Gauge attachments.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A126, Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

      - MSS-SP-67, Butterfly Valves.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Drawings must show or indicate the following:

      - Devices and their components, including connections, piping, fittings and control devices, as well as details concerning the factory mounted or assembled on site;

      - The schematic diagrams and actual wiring;

      - Dimensions and recommended installation instructions;

      - Curves and actual performance characteristics of pumps;

    - Submit pump curves showing the operating point, for verification

    - Submit detailed wiring diagrams of control systems established by the manufacturer, indicating the wiring and equipment installed at the factory on equipment or necessary piece to controls auxiliary equipment, parts and accessories regulators

    - Shop drawings must indicate the final location during assembly on site, control devices, piping, valves and fittings shipped separately by the hardware vendor

  - Instruction and Maintenance Manual

    - Supply the required manuals and incorporate them into an “Instruction and Maintenance Manual”.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure and/or capacity.

      - All details relating to the operation, care and maintenance of component;

      - A list of recommended spare parts and the names and addresses of suppliers.

- PART 2 – PRODUCT

- Furnish and install, as shown on plans, a ZY200-115 __________ as manufactured by Flo Fab Inc.

- Series F115 (Globe) & F1115 (Angle)

- The Pressure Reducing Control Valve shall be a pilot operated diaphragm valve designed to automatically reduce a ﬂuctuating higher upstream pressure to a constant lower downstream pressure regardless of vary- ing ﬂow rates.

- The main valve shall be a hydraulically operated, single diaphragm actuated, globe or angle pattern valve. Y-pattern valves shall not be permitted. The valve shall contain a disc and diaphragm assembly that forms a sealed chamber below the valve cover, separating operating pressure from line pressure. The diaphragm shall be constructed of nylon reinforced Buna-N, and shall not seal directly against the valve seat and shall be fully supported by the valve body and cover. Rolling diaphragm construction will not be allowed and there shall be no pistons operating the main valve or any pilot controls.

- The main valve body and cover shall be Ductile Iron ASTM A536, and all internal cast components shall be Ductile Iron or CF8M (316) Stainless Steel. All Ductile Iron components, including the body and cover, shall be lined and coated with an NSF 61 Certiﬁed Epoxy Coating applied by the electrostatic heat fusion process. All main valve throttling components (valve seat and disc guide) shall be Stainless Steel.  The valve body and cover must be machined with a 360-degree locating lip to assure proper alignment.

- The disc and diaphragm assembly shall contain a Buna-N synthetic rubber “Quad Seal” that is securely re- tained on 3-1/2 sides by a disc retainer and disc guide. Diaphragm assemblies utilizing bolts or cap screws for component retention will not be permitted.

- The exposed portion of the Quad Seal shall contact the valve seat and seal drip-tight.  The disc and dia- phragm assembly must be guided by two separate bearings, one installed in the valve cover and one con- centrically located within the valve seat, to avoid deﬂection and assure positive disc-to-seat contact. Center guided valves will not be permitted. All necessary repairs shall be made from the top of the valve while the body remains in line.

- Pilot control systems for valves 3” and smaller shall contain a Flow Clean Strainer, Fixed Oriﬁce Closing Speed, Adjustable Opening Speed Control and Pressure Reducing Pilot. Pilot control systems for valves 4” and larger shall contain an external Y-Strainer, Fixed Oriﬁce Closing Speed, Pressure Reducing Pilot and Isolation Ball Valves on all body connections. All pilot control systems shall utilize copper tubing and brass ﬁttings regardless of valve size. The adjustment range of the pressure reducing pilot shall be 30-300 psi.

- The valve shall be Flo Fab ACV Model F115 or (Globe) or F1115 (Angle) pattern Pressure Reducing Control Valve.

- Other Flo Fab ACV Pressure Reducing  Control  Valves

- F115-3 / F1115-3        Pressure Reducing Valve with Hydraulic Check Feature

- F115-7 / F1115-7        Pressure Reducing Valve with Downstream Surge Control Feature

- F115-74 / F1115-74    Pressure Reducing Valve with Low Flow By-Pass

- Acceptable component: Flo Fab series 115-ZY200

- PART 3 – EXECUTION

  - Installation

    - Constant pressure system will be implemented by the project contractor.

    - All wiring will be implemented by the manufacturer's instructions and codes federal, provincial and local regulations.

    - Get the manufacturer to adjust the operation of the pumps. Adjust operating pressures as indicated in the description of the equipment.

    - Ensure that the pump run in the expected direction.

    - Install and adjust the controls.

    - The manufacturer shall provide the maintenance staff of the building instructions for operation of each pump and the system total.

  - On-site Verification

    - Check the power supply.

    - Check overload protection settings.

    - Fill pumps with liquid and jog to ensure they are rotating the proper direction.

    - Check setting and operation of the selectors' Hand-Off-Auto and control devices and security alarms sound and visuals, guards against overheating and other securities

    - Set the crushers and presses - packing mounted on the shaft of the impeller.

End of Section