- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Code de construction du Québec - Chapitre 1 », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to :

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME, Boiler and Pressure Vessel Code (BPVC), Section VIII.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A278M, Specification for Gray Iron Castings for Pressure-Containing Parts for Temperatures up to 345°C.

      - ASTM A516 / 516, Specification for Pressure Vessel Plates, Carbon Steel, for Moderate and Lower Temperature Service.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CSA B51, Boiler, Pressure Vessel, and Pressure Piping Code.

  - Product Data

    - Submit shop drawings and technical data in conformance with client’s instructions.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following :

      - A description of the major components; the manufacturer, a type, series or model number reference, year constructed, horsepower rating, flow and pressure, holding or heating capacity;

      - All details relating to the operation, and the care and maintenance;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

  - Automatic Air Vents

    - Air vent, float type standard body cast bronze or cast iron and fittings DN 1 / 8, designed for a rated working pressure of 1034 kPa (150 psi) and a temperature of 93 ° C (200 ° F) to be used for heat transfer systems to water only.

      - Usage :

        - Connect to radiators, baseboard convectors, unit heaters and /or other heating appliances;

        - To be installed on piping that is equal to or less than DN 2;

        - At other locations as indicated.

      - Acceptable component: Flo Fab series AA.

    - Air vent, float type industrial: cast iron fitting and DN 3 / 4, designed for a rated working pressure of 1034 kPa (150 psi) and a temperature of 121 ° C (250 ° F).

      - Float: solid material, designed for a temperature of 115 ° C (239 ° F).

      - Usage :

        - Connections to radiators, convectors, unit heaters and other heating device using the glycol water;

        - Tube diameter equal to or less than 2 with a DN coolant water-glycol mixture;

        - Tube diameter equal to or greater than 2-1/2 DN with all types of heat transfer;

        - At other locations as indicated.

      - Acceptable component: Flo Fab series MV.

    - Install a bronze ball valve at each air vent.

  - Air vents for expansion tank

    - Coupling the flow controller for air expansion tank

    - Service pressure: 1034 kPa (150 psi).

    - Service Temperature: 121°C (250°F).

    - Accessories: adjustable vent tube and manual vent valve incorporated.

    - Acceptable component: Flo Fab series MV.

- PART 3 – EXECUTION

  - General

    - Install fittings and accessories according to the wiring installation of the pipe and as recommended by the manufacturer. Connect the drain fittings and purge the drain nearest floor.

    - Provide adequate clearance to allow access to equipment for maintenance. If the final location would be different than the drawings, consult the owner before proceeding with the installation.

    - If eligible clearances cannot be met, consult the owner and comply with his directives.

    - Refer to installation drawings supplied by the manufacturer.

    - Make sure all the holes used to connect accessories and appliances, and the mass of the equipment operating status are consistent with indications of shop drawings.

    - If the items and related accessories are delivered in parts, the assembly team check with the manufacturer.

  - Air Vent

    - Provide points of elimination of air in the pipes and equipment, high points downstream, before each descent of the fluid and locations specifically identified.

    - Air vents shall conform to the details and will be equipped with an isolation valve

    - Install a ball valve upstream of the air vent in the case of industrial drains and connect the overflow pipe to drain the nearest floor.

Fin de section