- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Quebec Building Code – Chapter I», unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Buttwelding Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Drawings must show or indicate the following:

      - Devices and their components, including connections, piping, fittings and control devices, as well as details concerning the factory mounted or assembled on site;

      - The schematic diagrams and actual wiring;

      - Dimensions and recommended installation instructions;

      - Curves and actual performance characteristics of pumps;

    - Submit pump curves showing the operating point, for verification

    - Submit detailed wiring diagrams of control systems established by the manufacturer, indicating the wiring and equipment installed at the factory on equipment or necessary piece to controls auxiliary equipment, parts and accessories regulators

    - Shop drawings must indicate the final location during assembly on site, control devices, piping, valves and fittings shipped separately by the hardware vendor

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

  - Sump column pumps to lift rainwater

    - Power :

      - Flow : [____] L/s ([____] gal US/min);

      - Head : [____] kPa ([____] feet);

      - Discharge DN [____].

    - Pump (s) in Colum effluent with their brand motor FLO FAB should have a capacity as indicated. The liquid will be pumping water at a maximum operating temperature of 40 º C (104 º F). The pumps must be able to handle spherical solids of at least [____]" ([____] mm) diameter and the pump discharge must be standard collar vertical positions. Each pump is provided with a seal type gland mounted on a bronze wear ring. Fins at the pump rear housing of the drive must be opened and also develop a pressure differential. The pump shaft shall be stainless steel with bronze sleeve. The lubrication of bearings shall be grease producing a turnover of satisfaction. Each pump has pads on intervals of 48 "(1220 mm) lengths. The hardware should be stainless steel. The total length of the pumps required will be indicated on the plans.

    - Single-phase motors must be protected against overload.  Three phase motors must also be protected against an overload in the magnetic starter.

    - The engines will be mounted on a cast adapter. The motor shaft is steel and there will be a flexible coupling between the motor shaft and the pump.

    - Installation type [a pump] [two pumps], approved by CSA: cast iron, with open type impeller in cast iron, stainless steel shaft, mechanical seal single tree.

    - The set will form a compact unit including a cover adapted controls, a control panel and all useful hardware. Wiring between the panel and components will be the responsibility of the installer of pumps

    - The control panel is a NEMA-1 (USA) OR EEMAC-1 (CANADA) comprising:

      - Main switch on handle and on the door;

      - Sets of power fuses;

      - Magnetic starters with adjustable overload relay;

      - Transformer control if required with secondary fuses;

      - Operating mode selectors "Manual - Off - Auto" (1 per pump);

      - LEDs: Power light, pump functionality light;

      - Electrical alternator (duplex);

      - Terminal is planned for a dry contact for remote alarm;

      - Terminals for fleets;

      - A visual and audible high level alarm with dry contact remote input.

    - The starting and stopping of pumps will be controlled by [two] [three] fleets with lifts NO contacts connected to the control panel. The cables will be fleets of length [20] [30] [50] feet. A [third] [fourth] fleet will be used to report the highest level of well water and trigger the alarm. These fleets must also be provided with a tie ribbon of stainless steel for easy installation into a moist well

    - Order: mechanical switches and control unit for installation type [a pump] [two pumps].

    - Valves: Each pump shall be provided with a ball check valve, branded FLO FAB CB series. Each valve must be fitted with an NPT or flanged connection, designed for vertical and horizontal installations. The check valve must be specifically designed for handling sewage or effluent. The valve design shall be such that solids, fibrous material, abrasives, rags, etc., can pass through without the need for flow-cons flush. In the operation mode, the ball must not impede flow through the valve and must prevent deadlock. The ball must be made of iron coated hollow rubber or phenolic resisting materials that are normally found in sewers. The body of the access plate shall be cast iron, ASTM Class 30 and Class 125. All fasteners must be stainless steel 18-8.

    - A tank [____] [____] mm x mm deep x mm [____] ([____] "diameter x [____]" deep x [____] "thick) fiberglass reinforced polyester resin and branded FLO FAB FB series which will be designed as submersible pumps for dewatering, and effluent waters from sewage. Thickness of the wall must withstand a load of sand saturated with water of 120 psi ` and have a safety factor of 2. The support flange test must stick to at least 3’’ (76mm) radius of the basin. When the tank is securely fastened to a cement slab or the clamp is covered cement, it cannot come up or be lifted to the surface if the latter is faithful because of the confining pressure. The basin is capable of withstanding a maximum temperature of 66 º C (150 º F).

    - A tank [____] [____] mm x mm deep x mm [____] ([____] "diameter x [____]" deep x [____] "thick) polyethylene brand FLO FAB series PB will be designed as submersible pumps for dewatering, effluent or waters from sewage. This tank is equipped with ultra-thick wedges, to the test of cracking, and chipping; rot, of rust or corrosion. Because of its light weight, special equipment for handling isn’t required.

    - The rectangular steel lid [____] mm [____] mm length x width x [____] mm ([____] "L x [____]" width x thickness [____]”) or round [____] [____] mm x mm ([____] "diameter x [____]" thick) will include a manhole, vent, and the required holes for switches floats and will have two parts. It will be covered with a coat of alkyd primer. An access cover, minimum load capacity of 150 psi and size described in the plans must be provided by the manufacturer of the pump. Steel frame should be pushed back from 1 / 4 "steel with aluminum braces where needed. The door should open to over 105 degrees and remain in that position without external support (arm restraint available on request).

    - Acceptable Products: Flo Fab series SUP (for storm water).

    - Characteristics; Brand: Flo Fab:

      - Model : SUP;

      - Engine [s]: [____] HP, hermetic, with protection against overloads;

      - Electricity : [____] V / [____] ph]  / [____] Hz / [____] RPM;

      - Control Panel: SSP (Simplex) and DSP (Duplex);

      - Fleet system: model 720163, suspended, with weight # 720149.

    - Operation sequence: SSP (for Simplex) and DSP (for duplex). Pumps should be controlled by float switches for liquid level control operating through the control panel of the pump:

      - Fleet 1 (Level 1) stop(s) pump(s) and alternate.

      - Fleet 2 (level 2) from the P1 or P2.

      - Fleet 3 (level 3) from the pump P2 or P1.

      - Fleet 4 (high) alarm.

- PART 3 – EXECUTION

  - Installation

    - In each case, doing mechanical and electrical connections between the pump, motor and control devices, as indicated.

    - Ensure that all pump motor does not support the pipe.

    - Once assembly is complete and the cover plate in place, align the entire pumping vertical submerged pump in the sump.

    - Spread a layer of sand of 150mm under the tank sump.

    - Make sure the pump runs in the expected direction.

    - The check valve and the shut off valve must be installed at the end of the vertical discharge pipe so that there is no hammer on the valve when the pump stops.

    - Install and adjust the controls.

  - Quality control on site

    - Check the power supply.

    - Check protection devices starters.

    - Start the pump and ensure it operates safely and appropriately.

    - Check setting and operation of the selector "Manual - Auto-Stop" control devices and security alarms sound and visual devices for protection against overheating and other securities.

    - Adjust the flow to water-cooled bearings.

    - Set the crushers and presses - packing mounted on the shaft of the impeller.

  - Start-up

    - According to the provisions of Section [01810 - Commissioning], in terms of general requirements and the requirements of this section.

    - Procedure:

      - Check the power supply;

      - Check the heater power overload starter;

      - Start the pump, checking the operation of the impeller;

      - Ensure that it operates safely and efficiently;

      - Check the settings and the operation of safety devices, devices for protection against overheating, audible and visual alarms and similar devices;

      - Check switch operation "Manual - Off - Auto";

      - Check the operation of the alternator.

      - Regulate the flow of leaking water cooled bearings.

      - Adjust the seal of the shaft.

      - Adjust the leakage rate from the shaft seal as recommended by the manufacturer.

      - Regulate the flow of leaking water cooled bearings. Make sure there are no obstructions under the base.

      - Run the pump continuously for a period of 12 hours.

      - Check the installation and operation of mechanical seals and gaskets seals. Make necessary adjustments.

      - Correct alignment of pipes and ducts to ensure good flexibility at all times

      - Eliminate conditions that could lead to the development of cavitations, gas expansion, or air through the pump

      - Measure the pressure drop cross the screen to final output, when it is not dirty.

      - Replace gasket if the pump is used for degreasing system or for temporary heating

Fin de section