- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Régie du bâtiment du Québec - Chapter 1 », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to :

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME, Section VIII, Boiler and Pressure Vessel Code (BPVC).

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A278M, Specification for Gray Iron Castings for Pressure-Containing Parts for Temperatures up to 345°C.

      - ASTM A516 / 516M, Specification for Pressure Vessel Plates, Carbon Steel, for Moderate and Lower Temperature Service.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CSA B51, Vessel Code and Pressure Piping.

  - Submittals

    - Submit shop drawings and technical data in conformance with client’s instructions.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions, and incorporate them into the operation & maintenance manual.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components; the manufacturer, a type, series or model number reference, year constructed, pressure ;

      - All details relating to the operation, and the care and maintenance;

      - A list of recommended spare parts.

- PART 2 – PRODUCT

  - Closed type expansion tank

    - Expansion tank horizontal threaded fittings.

    - Capacity: [____] L ([____] gal).

    - Dimensions: [____] mm ([____] inches) long X ([____] [____] mm) in diameter, heavy plate ([____] [____] mm) thick [as shown] [____].

    - Construction

      - Welded shell, conforming to the ASME code, made of sheet high carbon steel for pressure vessels, equipped with curved ends galvanized after fabrication, tested at 860 kPa according to ASTM A516 / 516m.

      - Construction complies with Part VIII of the BPVS of ANSI / ASME, CSA Standard B51 and provincial regulations.

      - Submit registration certificates required by the [provincial authorities] [____].

    - Fittings and accessories

      - Connector to the system at the bottom.

      - Bleeder valve, nominal diameter DN [1] [____], with tap at the bottom.

      - Vent connector, nominal diameter DN [____], at the top.

      - Safety valve and fitting at the top, according to the manufacturer's recommendations.

      - [Window 305 mm x 406 mm (12 in. x 16 in.)] [port] inspection.

      - Fittings level indicator glass tube ½ inch (12 mm), mounted at points at [1 / 8th] [____] and [7 / 8th] [____] height of the reservoir, with indicator tube glass, safety devices, shut-off valve and drain valve.

    - Brackets with bolts [seismic devices to integrated] [____].

    - Acceptable Products: Flo Fab series CUS for hydronic system and cooling system, with steel fitting.

- PART 3 – EXECUTION

  - Installation

    - Install fittings and accessories according to the wiring installation of the pipe and as recommended by the manufacturer. Connect the drain fittings and purge the drain nearest floor.

    - Provide sufficient clearance for access to equipment for maintenance. If the final location should be different from that indicated on the schematics, then consult the owner before proceeding with the installation.

    - If there is insufficient clearances then advise the owner and comply with his directives.

    - Refer to installation drawings supplied by the manufacturer.

    - Check and adjust the pressure before starting the system, it must correspond to the minimum pressure of the system. (Filling pressure.).

    - Make sure all the holes used to connect accessories and appliances, and the mass of the equipment operating status are consistent with indications of shop drawings.

    - If the items and related accessories are delivered in parts, check assembly with the manufacturer.

End of Section