- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Régie du bâtiment du Québec - Chapter 1 », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to :

      - CAN1 - 4.1, Water heater gas accumulation which are below the maximum heat 75,000 Btu / h.

      - CAN1 - 4.3, Water heater gas flow, gas water heater instantaneous water heaters and large automatic gas storage.

      - CAN / CGA - B149.1, Natural gas installation code.

      - CAN / CGA - B149.2, Propane installation code.

      - CSA B51, Vessel code and Pressure Piping.

      - CAN/CSA - B139, Installation code for oil burning equipment.

      - CAN / CSA - B140.0, General Requirements for Oil Burning Equipment.

      - CSA B140.12, Domestic water heaters and pool heating oil.

      - CAN / CSA C22.2 n 110, Construction and testing of electric water heaters storage.

      - CAN / CSA - C191 Series, CSA Standards on Performance of Electric Storage Tank Water Heaters (Functional standards on water heaters electric storage).

      - CAN / CSA - C309, Performance Requirements for Glass-Lined Storage Tanks for Household Hot Water Service.

      - B.N.Q. 3560.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Drawings must show or indicate the following:

      - Devices and their components, including connections, piping, fittings and control devices, as well as details concerning the factory mounted or assembled on site.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCTS

  - Storage tank for domestic hot water with cement inside without stove

    - Dimensions and capacity [as indicated].

    - Envelope [vertical] [horizontal], made of steel, conforming to CSA B51, code ANSI / ASME on the "Unfired Pressure Vessels" and the standards and provincial regulations, can withstand water pressure / effective steam of 862 kPa (125 psi) and a maximum temperature of 121  C (250  F) appropriate certification required.

    - Cement-lined water-resistant, 20 mm (3 / 4 ") thick.

    - Window of 305 mm x 406 mm (12" x 16") according to ASME, equipped with a stamp seal.

    - Replaceable aluminum anodes in number and size to ensure protection of the reservoir during a period of 20 years.

    - Cribs: steel; at least 2 horizontal models.  Base or 3 legs for vertical model.

    - Insulation: refer to the section - Thermal Insulation for aircraft and related items.

    - 1 year standard warranty on the tank and 5 years on the waterproof cement.

    - Features :

      - Capacity: 	[____] litres ([____] gal US).

      - Tank size (as indicated) [____] [____] mm x mm long ([____] "diameter x [____] inch in length).

    - All water heaters must be fitted with safety valve, pressure and temperature in accordance with ASME Code, provided with a lifting mechanism (Watts 40 XL) and a vacuum breaker (Watts 36 A), installed at 305 mm (12 ") above the device to the cold water supply, a drain valve connection for connecting hose.

    - Adjust thermostats to 60  C (140  F).

    - Exchanger tubes without envelope.

      - General: [Steam-water] [water-water]. Heating fluid flowing through the tubes.

      - Equipment designed, constructed and tested in accordance with the requirements of reference standards cited below:

        - Collar: Steel, tested at a pressure of 862 kPa, to be welded to the tank

        - Head: steel with inlet and outlet flanges and sockets for receiving a threaded drain hose and a vacuum breaker;

        - Tubes: OD DN 3 / 4, stainless steel 304 or (316), with Teflon supports. Each tube must be welded to the tube sheet;

        - Tube plate: steel or stainless steel 304 (316);

        - Fouling factor: Waterside 0.001;

        - Characteristics (as indicated):

          - Primary refrigerant:

            - [Steam (dry unsaturated)]: 
Superheated [____]  C ([____]  F); 
[____] Flow kg / h ([____] Btu / h).
Inlet pressure kPa ([____] [____] psi).

OR

            - [Water]:
Temperature [____] [____]   C to C
([____]  F [____]  F);
[____] Rate L / s ([____] USGPM);
Pressure drop kPa ([____] [____] psi).

          - Secondary refrigerant:

            - Rate [___] L / s ([____] USGPM);
Temperature [___] [___]   C to C;
([____]  F [____]  F);
Pressure drop kPa ([____] [____] psi).

        - Pressure: 1034 kPa (150 psi) in the tubes.

    - Tank size (as indicated) [____] [____] mm x mm long ([____] "diameter x [____] inch in length)

    - Acceptable product: Flo Fab series RWU.

- PARTIE 3 – EXÉCUTION

  - Installation

    - Install the domestic water heater according to manufacturer's recommendations and requirements of applicable codes and authorities.

    - Cradles are used for receiving the tank upright. These cradles are each deposited on a concrete pad to provide a clearance of 200 mm between them and the ground

    - Supply and install structural steel elements required for assembly of tanks and heaters - water

    - Provide a drain valve piped to nearest floor drain.

    - Magnesium anodes provide for the protection of tanks for a period of 20 years.  Place in locations easily accessible for replacement.

    - Provide a vacuum breaker on the cold water inlet, installed according to standards, to ensure protection against siphoning.

    - The heater equipped with a safety valve, a pressure and temperature ASME certified, factory installed.

    - Adjust thermostats to 60C (140F).

End of section