- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Régie du bâtiment du Québec - Chapter 1 », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to :

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME, Section VIII, Boiler and Pressure Vessel Code (BPVC).

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A278M, Specification for Gray Iron Castings for Pressure-Containing Parts for Temperatures up to 345°C.

      - ASTM A516 / 516M, Specification for Pressure Vessel Plates, Carbon Steel, for Moderate and Lower Temperature Service.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CSA B51, Code des chaudières, appareils et tuyauteries sous pression.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions, and incorporate them into the operation & maintenance manual.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCTS

  - Air purge

    - The Contractor shall provide and install, as indicated on plans and specifications, one or more air purge in compact line.

    - The design and fabrication will conform to ASME Section VIII Division 1 and CSA B51 relating to pressure vessels used at 150 psi (1034 kPa) and 550 ° F (288 ° C) maximum.

    - The inlet and outlet of each vessel will be equipped with an aperture of [____] inch ([____] mm) [Flanged].

    - The vessels will be equipped with separated superior NPT connector(s) for evacuation of air and lower connector(s) for other connections, such as components of pressure control (CPC).

    - Acceptable Products: Flo Fab series SEP (Suffix F flange) (suffix G for Grooved) (Suffix L with mounting brackets) and / or (Suffix F-4 stainless steel screen 304) (Suffix F-6 stainless steel screen 316).

- PARTIE 3 – EXECUTION

  - General

    - Install the tank and associated parts in accordance with installation diagram of the pipe and as recommended by the manufacturer. Connect the vent fittings and bleed.

    - Provide adequate clearance to allow access to equipment for maintenance. If the final location would be different than the drawings, consult the owner before proceeding with the installation.

    - If eligible clearances cannot be met, consult the owner and comply with its directives.

    - Refer to installation drawings supplied by the manufacturer.

    - Check and adjust the pressure before starting the system, it must correspond to the minimum pressure of the system. (Filling pressure).

    - Make sure all the holes used to connect accessories and appliances, and the mass of the equipment operating status are consistent with indications of shop drawings.

    - If the items and related accessories are delivered in parts, check assembly method with the manufacturer.

End of section