- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Régie du bâtiment du Québec - Chapter 1 », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to :

      - CAN1 - 4.1, Water heater gas accumulation which are below the maximum heat 75,000 Btu / h.

      - CAN1 - 4.3, Water heater gas flow, gas water heater instantaneous water heaters and large automatic gas storage.

      - CAN / CGA - B149.1, Natural gas installation code.

      - CAN / CGA - B149.2, Propane installation code.

      - CSA B51, Vessel code and Pressure Piping.

      - CAN/CSA - B139, Installation code for oil burning equipment.

      - CAN / CSA - B140.0, General Requirements for Oil Burning Equipment

      - CSA B140.12, Domestic water heaters and pool heating oil.

      - CAN / CSA C22.2 n 110, Construction and testing of storage electric water heaters.

      - CAN / CSA - C191 Series, CSA Standards on Performance of Electric Storage Tank Water Heaters (Functional standards on water heaters electric storage).

      - CAN / CSA - C309, Performance Requirements for Glass-Lined Storage Tanks for Household Hot Water Service.

      - B.N.Q. 3560.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Drawings must show or indicate the following:

      - Devices and their components, including connections, piping, fittings and control devices, as well as details concerning the factory mounted or assembled on site.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCTS

  - Blow off tank

    - Dimensions and capacity [as indicated].

    - Envelope [vertical] [horizontal], made of steel, conforming to CSA B51, code ANSI / ASME on the "Unfired Pressure Vessels" and the standards and provincial regulations, can withstand water pressure / effective steam of 862 kPa (125 psi) and a maximum temperature of 121  C (250  F) appropriate certification required.

    - Window of 100 mm x 150 mm (4 "x 6"), for reservoir 24 inches or less and 305 mm x 406 mm (12 "x 16") with ASME stamp provided with a seal.

    - Cribs: steel; at least 2 horizontal models.  Base or 3 legs for vertical model.

    - 1 year standard warranty on the tank.

    - Features :

      - Capacity: 	[____] litres ([____] gal US).

      - Tank size (as indicated) [____] mm diameter x [____] mm long ([____] inch diameter x [____] inch in length).

    - Expansion tanks must be installed between the boiler and drain with cold water supply and vent in order to reduce the pressure and temperature of the water went away to the sewer.

    - Acceptable product: Flo Fab series BLO.

- PARTIE 3 – EXÉCUTION

  - Installation

    - Install the tank according to manufacturer's recommendations and requirements of applicable codes and authorities.

    - Cradles are used for receiving the tank upright. These cradles are each deposited on a concrete pad to provide a clearance of 200 mm between them and the ground

    - Supply and install structural steel elements required for assembly of tanks.

    - Provide a drain valve piped to nearest floor drain.

    - The tank should be equipped with a safety valve, with pressure and temperature ASME certified, factory installed.

    - Provide the electrical connection under Section 16 of the spec.

End of section