Specification for Installer Friendly Series® Single Phase Control Panel

- Must be available in either simplex or duplex models.

- Incoming pump power shall be single-phase, 60 Hz, 120/208/240 volts AC.

- Incoming control/alarm power shall be single-phase, 60 Hz, 120 volts AC.

- Easy to use touch pad for programming pump control.

- The control panel is to have models available that interface with float input and models available that interface with transducer input.

- Float-operated models shall incorporate three (3), or four (4), normally open, mercury or mechanically-activated control switches with pipe clamps. Inputs shall be labeled in the panel as stop, lead, lag/alarm, and alarm for demand dose and redundant off, timer enable, high alarm, and timer override (timed dose models). Floats shall be FLO FAB  control switches or approved equal.

- Transducer-operated models shall incorporate FLO FAB  sensor.

- The control panel is to have a means to be configured in the field to operate as either a time dose or demand dose panel.

- The control panel is to be equipped with separately fused alarm and control circuits.

- The control panel is to be equipped with float status indicators, pump run indicators, Hand – Off – Auto status indicators, and power on indicators.

- Panel must log the following data: Pump run time, cycle counts, alarm counts, float out of sequence counts, and timer override counts (time dose only).

- Alarm must activate if floats operate out of sequence (float model) or if transducer circuit opens (C-Level™ sensor model).