SECTION 232123 - HYDRONIC PUMPS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Vertical Turbine centrifugal pumps.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - Buna-N: Nitrile rubber.

        - EPT: Ethylene propylene terpolymer.

        - NPSH: Net positive suction head.

        - VFC: Variable-frequency controller(s).

      - ACTION SUBMITTALS

        - Product Data: For each type of product indicated.

          - Include certified performance curves and rated capacities, operating characteristics, furnished specialties, electrical characteristics, and accessories for each type of product indicated.

          - Indicate pump's final impeller dimensions, and operating point on curves.

        - Shop Drawings: For each product indicated.  For pump packages include plans, elevations, sections, details, and attachments to other work.

          - Show pump layout, component layout and connections.

          - Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, model numbers, and location and size of each field connection.

          - Wiring Diagrams: For power, signal, and control wiring.

      - INFORMATIONAL SUBMITTALS

Retain "Performance Tests" paragraph below if retaining certification in "Quality Assurance" Article.

        - Performance Tests: For optional production performance tests in "Quality Assurance" Article.

        - Field Quality-Control Reports: Startup service reports.

        - Sample Warranty: For manufacturer's warranty.

      - CLOSEOUT SUBMITTALS

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Operation and Maintenance Data: For pumps to include in emergency, operation, and maintenance manuals.

          - Exploded view diagrams with component parts list.

          - Instructions for installation, start-up, and operation.

          - Description of maintenance and care procedures.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise "Mechanical seals", "Bearing sets" and "Couplings" Subparagraphs below to suit Project.

          - Mechanical seals: [One] <Insert number> mechanical seal(s) for each pump.

          - Bearing sets: [One] <Insert number> bearing set(s) for each pump.

          - Couplings: [One] <Insert number> coupling(s) for each pump.

      - QUALITY ASSURANCE

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain the following paragraph for optional acceptance tests by the manufacturer.  See the following website link for test details:

http://www.flofab.com/HomeSite/Literature/Documents/Certificates/Hydraulic%20Performance%20Tolerence/Brochure/en/?SessionNoClient=1347&SessionAdministrator=0

        - Production Performance Acceptance Tests:

          - ANSI/HI 14.6, Hydraulic Institute Performance Acceptance Tests: Five test points at levels 2B, 2U, or 3B.

          - Certified NPSH curve.

          - Factory witness test.

          - Certified motor test.

        - ASME Compliance:

          - ANSI/ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

          - ANSI/ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

          - ANSI/ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

          - ANSI/ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

          - ANSI/ASME B18.2.1, Square and Hex Bolts and Screws.

          - ANSI/ASME B18.2.2, Square and Hex Nuts.

        - ASTM Compliance:

          - ASTM A47 / A47M, Specification for Ferritic Malleable Iron Castings.

          - ASTM A48 / A48M, Standard Specification for Gray Iron Castings.

          - ASTM A53 / A53M, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

          - ASTM A536, Specification for Ductile Iron Castings.

          - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

          - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

        - AWWA Compliance:

          - ANSI/AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

        - CSA Compliance:

          - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

          - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

      - WARRANTY

Visit the website for a copy of the warranty and exclusions:

http://www.flofab.com/HomeSite/Literature/Documents/ARRA,%20Terms%20and%20conditions/Terms%20and%20Conditions/Brochure/en/Flo%20Fab%20Standard%20Terms%20and%20Conditions%20of%20Sale%20US%2011%20March,16.pdf

- Manufacturer's Warranty: Manufacturer undertakes during the period of warranty to
repair or to replace with new, in the shortest time possible, any parts found to present recognized defects in materials, construction or workmanship that render them unfit for the intended use.  The warranty on the products has the following duration from the date of shipping the material to job site:

          - Pumps: 5 years.

          - Packaged Systems: 8 years.

      - DELIVERY, STORAGE, AND HANDLING

        - Retain protective coatings and flange's protective covers during storage.

      - COORDINATION

        - Coordinate sizes and locations of concrete bases with actual equipment provided.

- PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

      - SEPARATELY COUPLED, VERTICALLY MOUNTED, TURBINE CENTRIFUGAL PUMPS

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; 7000 series or comparable product by the following;

        - Description: Factory-assembled and -tested, [single-stage] [multistage], centrifugal, impeller-between-bearings, end-suction pump as defined in HI 2.1-2.2 and HI 2.3; designed for installation with pump and motor shafts mounted vertically and projecting into a sump.

        - See Pump schedule for details

        - Pump Construction:

          - Pump Bowl: Cast iron, with [cone] [basket] strainer[, replaceable bronze wear ring,] and suction bell.[ Water passages of intermediate bowls shall be coated with porcelain enamel.]

          - Impeller: ASTM B 584, cast bronze; statically and dynamically balanced and keyed to shaft. For pumps not frequency-drive controlled, trim impeller to match specified performance.

          - Pump Shaft: [Carbon] [Stainless] steel sized according to manufacturer's requirements.

          - Pump Bearings: Water-lubricated bronze and rubber sleeve bearings in cast-iron housing.

          - Pump Column: ASTM A 53/A 53M, Grade B steel pipe.

Retain one of two "Seal" subparagraphs below. Retain first subparagraph for service temperatures above 200 deg F (93 deg C); retain second subparagraph for service temperatures 200 deg F (93 deg C) or lower. In first subparagraph below, retain "Buna-N" option for temperature rating of 225 deg F (107 deg C); retain "EPT" option for 250 deg F (120 deg C) and for glycol solutions.

          - Seal: Mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and [Buna-N] [EPT] bellows and gasket. Include water slinger on shaft between motor and seal.

          - Seal: Packing seal consisting of stuffing box with a minimum of four rings of graphite-impregnated braided yarn with bronze lantern ring between center two graphite rings, and bronze packing gland.

        - Shaft Coupling: Keyed with locking collets.

        - Discharge Head: ASME B16.1, [Class 125] [Class 250] discharge flange with threaded gage tapping. Top of discharge head shall have a registered fit to accurately locate the driver.

        - Drive Ratchet: Non reversing ratchet.

        - Hollow Shaft Motor: Single speed and secured to discharge head.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, drip proof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, non ventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

            - Motor Bearings: Grease lubricated.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient.

            - NEMA Design: <Insert designation>.

            - Service Factor: <Insert value>.

If Project has more than one type or configuration of separately coupled, vertically mounted, turbine centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Minimum Static Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: 175 psig (1204 kPa).

          - Maximum Continuous Operating Temperature: 200 deg F (93 deg C).

          - Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: [120] [240] [208] [460] [575]<Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

- EXECUTION

      - EXAMINATION

Retain first two paragraphs below if required.

        - Examine roughing-in for piping systems to verify actual locations of piping connections before pump installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PUMP INSTALLATION

In first paragraph below, retain "HI 1.4" option for centrifugal pumps and "HI 2.4" option for vertically mounted, turbine centrifugal pumps.

        - Comply with [HI 1.4] [and] [HI 2.4].

        - Install pumps to provide access for periodic maintenance including removing motors, impellers, and accessories.

        - Independently support pumps and piping so weight of piping is not supported by pumps and weight of pumps is not supported by piping.

        - If the Pump is mounted on base: providing templates for determining the location of anchor bolts and sleeves, level pump by utilizing the necessary shims and encase the base cement.

Retain "Equipment Mounting" Paragraph below for in-line pumps suspended from structure.

        - Equipment Mounting:

- Install vertical pumps with continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of size required to support weight of pumps.

          - Comply with requirements for seismic-restraint devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

          - Comply with requirements for hangers and supports specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."Retain this article only for separately coupled, end- and double-suction centrifugal pumps.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with requirements for piping specified in Section 232213 "Steam and Condensate Heating Piping" and Section 232216 Steam and Condensate Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Where installing piping adjacent to pump, allow space for service and maintenance.

        - Connect piping to pumps. Install valves that are same size as piping connected to pumps.

        - Install suction and discharge pipe sizes equal to or greater than diameter of pump nozzles.

        - Install [check, shutoff, and throttling valves] [check valve and throttling valve with memory stop] [triple-duty valve] on discharge side of pumps.

        - Install [Y-type strainer] [suction diffuser] and shutoff valve on suction side of pumps.

        - Install pressure gages on pump suction and discharge or at integral pressure-gage tapping, or install single gage with multiple-input selector valve.

Retain first two paragraphs below for automatic condensate pump units.

        - Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

      - STARTUP SERVICE

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks according to manufacturer's written instructions.

          - Check piping connections for tightness.

          - Clean strainers on suction piping.

          - Perform the following startup checks for each pump before starting:

            - Verify bearing lubrication.

            - Verify that pump is free to rotate by hand and that pump for handling hot liquid is free to rotate with pump hot and cold. If pump is bound or drags, do not operate until cause of trouble is determined and corrected.

            - Verify that pump is rotating in the correct direction.

          - Prime pump by opening suction valves and closing drains, and prepare pump for operation.

          - Start motor.

          - Open discharge valve slowly.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain hydronic pumps.

END OF SECTION 232123