- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / API 609, Lug and Wafer Type Butterfly Valves.

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

      - ANSI / ASME B16.22, Wrought Copper and Copper-Alloy Solder Joint Pressure Fittings.

      - ANSI / ASME B16.25, Butt welding Ends.

      - ANSI / ASME B16.34, Valves – Flanged, Threaded and Welding Ends.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / ASME B40.1, Pressure Gauges and Gauge attachments.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A126, Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

      - MSS-SP-67, Butterfly Valves.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Drawings must show or indicate the following:

      - Devices and their components, including connections, piping, fittings and control devices, as well as details concerning the factory mounted or assembled on site;

      - The schematic diagrams and actual wiring;

      - Dimensions and recommended installation instructions;

      - Curves and actual performance characteristics of pumps;

    - Submit pump curves showing the operating point, for verification

    - Submit detailed wiring diagrams of control systems established by the manufacturer, indicating the wiring and equipment installed at the factory on equipment or necessary piece to controls auxiliary equipment, parts and accessories regulators

    - Shop drawings must indicate the final location during assembly on site, control devices, piping, valves and fittings shipped separately by the hardware vendor

  - Instruction and Maintenance Manual

    - Supply the required manuals and incorporate them into an “Instruction and Maintenance Manual”.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure and/or capacity.

      - All details relating to the operation, care and maintenance of component;

      - A list of recommended spare parts and the names and addresses of suppliers.

- PART 2 – PRODUCT

  - Water booster for domestic water, constant speed, without Hydro-Pneumatic expansion tank

    - Provide and install a booster system, pre-assembled, tested and factory assembled. Each pumping system shall include, as a minimum, a control panel, pressure switches, and two pumps and motor assemblies. The system package shall also included pressure reducing valve, isolation valves, and pressure gauges, frame, interconnecting piping, and a constant speed control system.

    - The pumps are of the type:

      - Vertical-in-Line Circulation Pumps

      - Volute: cast iron (bronze for domestic hot water), threaded or flanged suction and discharge connections.  Both end connections are 180° from each other.

      - Impeller: stamped brass or cast bronze, dynamically balanced, with a minimum clearance.

      - Shaft: stainless steel, fitted with bronze bushing and a butane rubber O-ring.

      - Sealing: Ceramic and carbon mechanical seal good to a working temperature of 135°C (275°F).

      - Motor: respecting the requirements of Section 15010.

      - Maximum Working Pressure: 862 kPa (125 psi).

      - Maximum Working Temperature: 107°C (225°F).

      - Size and Capacity: As specified on pump tables shown on plans and specifications.

      - Acceptable component: Flo Fab Series 700.

    - The capability of the booster group is shown in the list of equipment.

    - The booster group must be provided with a constant speed control panel NEMA-1 (USA) or EEMAC-1 (CANADA) pre-assembled and  pre-spun at the factory and includes the following:

      - Control operated from the outside of the housing;

      - Full voltage magnetic starters with overload protection combined with fuse and fuse holder;

      - Minimum run timers

      - Overload protection on each phase equipped with an auxiliary contact NO and NC auxiliary contact pre-spun plate terminal identified;

      - Transformer control circuit with secondary breaker;

      - Pressure switch (PS)

      - Minimum timer running from 0 to 10 minutes, for each pump;

      - Selector: "Manual - Off - Auto" for each pump;

      - Lights:

• Powered
• Walk
• Low pressure
• Overload

      - Pressure switch trip point adjustable timer 0-60 seconds for the shutdown of the pump on a low suction pressure.

      - Acceptable component: Flo Fab Series DP.

    - Butterfly valves are of type:

      - Butterfly valves with a diameter equal to or greater than DN 2 1 / 2, Model without flange, with wing

      - Compliant MSS SP 67, Class 150, Class 1 MPa type EHG, body in cast iron, stainless steel valve, stainless steel stem, EPDM seat, replaceable, lever and locking lever, control gear in, for valves with a diameter greater than DN 6.

      - Maximum service pressure: 1034 kPa (150 psi).

      - Maximum service temperature: 108°C (225°F).

      - Acceptable component: Flo Fab Series BFVZ.

    - The check valves are of type:

      - Silent Check Valves

        - Valves with a diameter equal to or greater than 2-1/2 DN without flanges.

          - Class 125, Class 862 kPa (125psi), body iron or cast iron, bronze internal parts, stainless steel spring (spring, heavy duty in the case of assemblies on risers down flow).

          - Acceptable component: Flo Fab Series LSDDB.

    - The pressure reducing valves is of type:

        - Valves with a diameter equal to or greater than 2 DN with flanges.

        - The valves are pilot operated, diaphragm type and hydraulically operated.

          - Class 125, Class 862 kPa (125psi), body iron or cast iron, bronze internal parts, with pilot and check valve, heavy duty in the case of assemblies on risers down flow).

          - Acceptable component: Flo Fab Series ZY200.

    - An automatic proportional purge detects excess temperature and allows the purging of a specified quantity of water to the drain.

    - The gauges look like:

      - Dial-type gauges 4 "(100 mm) diameter, conforming to ANSI / ASME B40.1, Grade 2A, accurate to within 1%, unless otherwise indicated.

      - The gauges have a housing and a stainless steel ring polished. The movement is also stainless steel. The needle is adjustable (adjustable micrometer)

      - These gauges are calibrated so as to operate in the center of their graduation. Normally, graduation will be combined from 0 to 690 kPa (0 to 100 psi)

      - Acceptable component: Flo Fab Series RFF0400LF.

    - Operation of the pump (duplex).

      - The controls operate as follows:

        - The pump P-1 will run continuously and does not stop. Should the demand increase then the second pump P-2 will be energized to satisfy the demand. When the demand decrease, the second pump will stop and only P-1 will continue to operate. There is a temperature purge to protect the pumps from overheating. The pumps can be controlled manually

    - The booster pump system will be connected to the collectors of suction and 304 stainless steel and fitted with the system controller includes a constant speed  to form a pumping fully autonomous pre yarn, pre adjusted and tested before shipment to the conditions specified above

    - A substantial foundation will be provided to absorb vibration and provide a solid support system. Suitable fixing bolts are embedded in concrete with sockets to allow adjustment of the bolts after the concrete has been poured. The system will be placed on this foundation, carefully levelled and the bolts tightened.

    - The capabilities of the Duplex booster group are shown in the list of equipment.

    - Acceptable components : Flo Fab Series D-CPS-700-DP

- PART 3 – EXECUTION

  - Installation

    - Constant pressure system will be implemented by the project contractor.

    - All wiring will be implemented by the manufacturer's instructions and codes federal, provincial and local regulations.

    - Get the manufacturer to adjust the operation of the pumps. Adjust operating pressures as indicated in the description of the equipment.

    - Ensure that the pumps run in the expected direction.

    - Install and adjust the controls.

    - The manufacturer shall provide the maintenance staff of the building instructions for operation of each pump and the system total.

  - On-site Verification

    - Check the power supply.

    - Check overload protection settings.

    - Fill pumps with liquid and jog to ensure they are rotating the proper direction.

    - Check setting and operation of the selectors' Hand-Off-Auto and control devices and security alarms sound and visuals, guards against overheating and other securities

    - Set the crushers and presses - packing mounted on the shaft of the impeller.

End of Section