- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / API 609, Lug and Wafer Type Butterfly Valves.

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Buttwelding Fittings.

      - ANSI / ASME B16.22, Wrought Copper and Copper-Alloy Solder Joint Pressure Fittings.

      - ANSI / ASME B16.25, Butt welding Ends.

      - ANSI / ASME B16.34, Valves – Flanged, Threaded and Welding Ends.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / ASME B40.1, Pressure Gauges and Gauge attachments.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A126, Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

      - MSS-SP-67, Butterfly Valves.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Drawings must show or indicate the following:

      - Devices and their components, including connections, piping, fittings and control devices, as well as details concerning the factory mounted or assembled on site;

      - The schematic diagrams and actual wiring;

      - Dimensions and recommended installation instructions;

      - Curves and actual performance characteristics of pumps;

    - Submit pump curves showing the operating point, for verification

    - Submit detailed wiring diagrams of control systems established by the manufacturer, indicating the wiring and equipment installed at the factory on equipment or necessary piece to controls auxiliary equipment, parts and accessories regulators

    - Shop drawings must indicate the final location during assembly on site, control devices, piping, valves and fittings shipped separately by the hardware vendor

  - Instruction and Maintenance Manual

    - Supply the required manuals and incorporate them into an “Instruction and Maintenance Manual”.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure and/or capacity.

      - All details relating to the operation, care and maintenance of component;

      - A list of recommended spare parts and the names and addresses of suppliers.

- PART 2 – PRODUCT

  - Water booster for domestic water, constant speed, with Hydro-Pneumatic expansion tank

    - Provide and install a booster system, pre-assembled, tested and factory assembled. Each pumping system shall include, as a minimum, a control panel, pressure switches, hydro-pneumatic expansion tank and a pump and motor assembly. The system package shall also included pressure reducing valve, isolation valves, and pressure gauges, frame, interconnecting piping, and constant speed control system.

    - The pump is of the type:

      - Vertical-in-Line Pump

      - Volute: Cast Iron Class 30 (ASTM No. A 159), suction and discharge side flanged connections. Threaded connections for pressure gauges at the inlet and discharge flanges, for venting and draining, and for optional thermometer. A pitot tube type flowmeter, Flo Fab series FMI, can be supplied and installed on the discharge of the volute, taking differential pressure readings and confirming pump capacity. Incorporated in the volute casting is a solid base with four anchor holes and a connection to drain that can accommodate a valve with bronze cap, model HN0050. The volute includes a wear ring that is replaceable. Maximum operating pressure is 1200 kPa (175 psi).

      - Impeller: Cast Bronze (ASTM No. B 584), closed type, dynamically balanced, keyed to the stainless steel shaft and secured by a stainless steel bolt and washer.

      - Shaft: stainless steel, fitted with bronze sleeve and butane O-ring.

      - Sealing: The wet-end components are sealed with a self-lubricating mechanical seal. The seal is composed of a ceramic seat, a rotating carbon ring, a viton bellow and all other materials in stainless steel. It is designed for continuous operation at maximum working temperature of 400°F (205°C) corresponding to a maximum working pressure of 1724 kPa (250 psi).

      - Coupling: No coupling design, impeller is directly coupled to the motor shaft.

      - Motor: respecting the requirements of Section 15010. Motor and pump are designed for vertical mounting. Motors equipped with grease lubricated heavy duty ball bearings, suitable for maximum loads created by the pump. Motor type JM, high performance class B with a safety factor of 1.15.

      - Selection of motor will allow the pump to operate at maximum capacity without surpassing the maximum amperage draw on the motor.

      - Each pump is hydrostatically tested.

      - Size and Capacity: As specified on pump tables shown on [plans] [specifications].

      - Acceptable component: Flo Fab series 880.

    - The capability of the booster group is shown in the list of equipment.

    - Replaceable bladder Hydro-pneumatic expansion tank

      - Vertical Cylindrical expansion tank with replaceable bladder.

      - Full acceptance volume: As indicated on the expansion tank table.

      - Bladder is able to resist temperatures up to 115°C (240°F).

        - BUTYL for portable water

      - Design pressure: 862 kPa (125 psi) for tanks constructed in accordance with the ASME, Section VIII, Div. 1 and thus will be stamped with the ASME Logo.

      - Pre-Charge : Initial system air pressure:

        - For Booster systems: pre-charge is equal to the “cut-in” of the pump.

      - Vertical base.

      - Approved model :

        - Flo Fab model BT for hydro-pneumatic systems incorporating stainless steel connection.

    - The booster group must be provided with a constant speed control panel NEMA-1 (USA) or EEMAC-1 (CANADA) pre-assembled and  pre-spun at the factory and includes the following:

      - Control operated from the outside of the housing;

      - Full voltage magnetic starter with overload protection combined with fuse and fuse holder;

      - Minimum run timer

      - Overload protection on each phase equipped with an auxiliary contact NO and NC auxiliary contact pre-spun plate terminal identified;

      - Transformer control circuit with secondary breaker;

      - Pressure switch (PS)

      - Minimum timer running from 0 to 10 minutes, auxiliary pump;

      - Selector: "Manual - Off - Auto" for the pump;

      - Lights:

• Powered
• Walk
• Low pressure
• Overload

      - Pressure switch trip point adjustable timer 0-60 seconds for the shutdown of the pump on a low suction pressure.

      - Acceptable component: Flo Fab series SP.

    - Butterfly valves are of type:

      - Butterfly valves with a diameter equal to or greater than DN 2 1 / 2, Model without flange, with wing

      - Compliant MSS SP 67, Class 150, Class 1 MPa type EHG, body in cast iron, stainless steel valve, stainless steel stem, EPDM seat, replaceable, lever and locking lever, control gear in, for valves with a diameter greater than DN 6.

      - Maximum service pressure: 1034 kPa (150 psi).

      - Maximum service temperature: 108°C (225°F).

      - Acceptable component: Flo Fab series BFVZ.

    - The check valve is of type:

      - Silent Check Valve

        - Valves with a diameter equal to or greater than 2-1/2 DN without flanges.

          - Class 125, Class 862 kPa (125psi), body iron or cast iron, bronze internal parts, stainless steel spring (spring, heavy duty in the case of assemblies on risers down flow).

          - Acceptable component: Flo Fab series LSDDB.

    - The pressure reducing valve is of type:

        - Valve with a diameter equal to or greater than 2 DN with flanges.

        - The valve is pilot operated, diaphragm type and hydraulically operated.

          - Class 125, Class 862 kPa (125psi), body iron or cast iron, bronze internal parts, with pilot and check valve, heavy duty in the case of assemblies on risers down flow).

          - Acceptable component: Flo Fab series ZY200.

    - An automatic proportional purge detects excess temperature and allows the purging of a specified quantity of water to the drain.

    - The gauges look like:

      - Dial-type gauges 4 "(100 mm) diameter, conforming to ANSI / ASME B40.1, Grade 2A, accurate to within 1%, unless otherwise indicated.

      - The gauges have a housing and a stainless steel ring polished. The movement is also stainless steel. The needle is adjustable (adjustable micrometer)

      - These gauges are calibrated so as to operate in the center of their graduation. Normally, graduation will be combined from 0 to 690 kPa (0 to 100 psi)

      - Acceptable component: Flo Fab series RFF0400LF.

    - Operation of the pump (simplex).

      - The controls operate as follows:

        - The pump will run continuously if there is a demand. At low or no flow the pump will charge the Hydro-tank with the maximum water pressure. Pump de-energize when maximum stored water quantity is reached. Tank supplies water to the building while the pump remains off. When the tank reaches a point of minimum water, the pump is energized by a differential PS-2 pressure switch to meet building demands and recharge the tank. The pump cycle through minimum run timer. As water is released from the bladder tank and the pressure is required, the pressure switch PS-1 is activated and operates the pump. This is an energy saving function permitting the pump to be inactive during no or low flow If the suction pressure drops to a dangerously low level, a switch will prevent the pump from running. The pump can be controlled manually

    - The booster pump system will be connected to the collectors of suction and 304 stainless steel and fitted with the system controller includes a constant speed  to form a pumping fully autonomous pre yarn, pre adjusted and tested before shipment to the conditions specified above

    - A substantial foundation will be provided to absorb vibration and provide a solid support system. Suitable fixing bolts are embedded in concrete with sockets to allow adjustment of the bolts after the concrete has been poured. The system will be placed on this foundation, carefully levelled and the bolts tightened.

    - The capabilities of the Simplex booster group are shown in the list of equipment.

    - Acceptable components : Flo Fab series S-CPS-880-BT-SP

- PART 3 – EXECUTION

  - Installation

    - Constant pressure system will be implemented by the project contractor.

    - All wiring will be implemented by the manufacturer's instructions and codes federal, provincial and local regulations.

    - Get the manufacturer to adjust the operation of the pumps. Adjust operating pressures as indicated in the description of the equipment.

    - Ensure that the pump run in the expected direction.

    - Install and adjust the controls.

    - The manufacturer shall provide the maintenance staff of the building instructions for operation of each pump and the system total.

  - On-site Verification

    - Check the power supply.

    - Check overload protection settings.

    - Fill pumps with liquid and jog to ensure they are rotating the proper direction.

    - Check setting and operation of the selectors' Hand-Off-Auto and control devices and security alarms sound and visuals, guards against overheating and other securities

    - Set the crushers and presses - packing mounted on the shaft of the impeller.

End of Section