- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / API 609, Lug and Wafer Type Butterfly Valves.

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Buttwelding Fittings.

      - ANSI / ASME B16.22, Wrought Copper and Copper-Alloy Solder Joint Pressure Fittings.

      - ANSI / ASME B16.25, Butt welding Ends.

      - ANSI / ASME B16.34, Valves – Flanged, Threaded and Welding Ends.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / ASME B40.1, Pressure Gauges and Gauge attachments.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A126, Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

      - MSS-SP-67, Butterfly Valves.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Drawings must show or indicate the following:

      - Devices and their components, including connections, piping, fittings and control devices, as well as details concerning the factory mounted or assembled on site;

      - The schematic diagrams and actual wiring;

      - Dimensions and recommended installation instructions;

      - Curves and actual performance characteristics of pumps;

    - Submit pump curves showing the operating point, for verification

    - Submit detailed wiring diagrams of control systems established by the manufacturer, indicating the wiring and equipment installed at the factory on equipment or necessary piece to controls auxiliary equipment, parts and accessories regulators

    - Shop drawings must indicate the final location during assembly on site, control devices, piping, valves and fittings shipped separately by the hardware vendor

  - Instruction and Maintenance Manual

    - Supply the required manuals and incorporate them into an “Instruction and Maintenance Manual”.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure and/or capacity.

      - All details relating to the operation, care and maintenance of component;

      - A list of recommended spare parts and the names and addresses of suppliers.

- PART 2 – PRODUCT

  - Water booster for domestic water, with variable speed, with tank

    - Provide and install a booster group piece, pre-assembled, tested and factory set, type three pumps, system controlled with three variable speed drives (VFD’S) and a bypass circuit with Hydropneumatic tank, supplied ready for connection to mechanical and electrical systems on site.

    - Vertical Multi-Stage Pumps

    - Volute: 316 Stainless Steel, suction and discharge side flanged connections.

    - Sealing: The wet-end components are sealed with a self-lubricating mechanical seal. The seal is composed of a ceramic seat, a rotating carbon ring, a viton bellow and all other materials in stainless steel. It is designed for continuous operation at maximum working temperature of 400°F (205°C) corresponding to a maximum working pressure of 1724 kPa (250 psi).

    - Impeller: 316 Stainless Steel, dynamically balanced, having minimum play.

    - Shaft: 316 Stainless Steel, fitted with bronze sleeve and butane O-ring.

    - Motors: respecting the requirements of Section 15010, NEMA specifications, closed type, high efficiency, and foot mounted.

    - Selection of motor will allow the pump to operate at maximum capacity without surpassing the maximum amperage draw on the motor.

    - Maximum Service Pressure:  2482 kPa (360 psi).

    - Maximum Service Temperature: 120°C (248°F).

    - Each pump is hydrostatically tested.

    - Size and Capacity: As specified on pump tables shown on plans       and specifications.

    - Acceptable component: Flo Fab series PSM

    - The capability of the booster group is shown in the list of equipment.

    - Operation of the pumps (triplex).

      - The controls operate as follows:

        - The pumps will run continuously. If there is a change of process variable, the pump speed will change. If the suction pressure drops to a dangerously low level, a switch will prevent the pumps from running. Should the discharge pressure continue to drop the second and third pumps will start and the speed will be controlled by the drive to maintain the required set pressure. The pumps can be controlled manually

    - Replaceable bladder expansion tank

      - [Horizontal] [Vertical] Cylindrical expansion tank with replaceable bladder.

      - Full acceptance volume: As indicated on the expansion tank table.

      - Bladder is able to resist temperatures up to 115°C (240°F).

        - BUTYL for portable water

      - Design pressure: 862 kPa (125 psi) for tanks constructed in accordance with the ASME, Section VIII, Div. 1 and thus will be stamped with the ASME Logo.

      - Pre-Charge : Initial system air pressure:

        - For Booster systems: pre-charge is equal to the “cut-in” of the pump.

      - [Horizontal saddle] [Vertical base].

      - Approved models :

        - Flo Fab models BT for hydro-pneumatic systems incorporating stainless steel connection.

    - The booster group must be provided with a control system triplex Variable Speed NEMA-1 (USA) or EEMAC-1 (CANADA) pre-assembled and pre-spun at the factory and includes the following:

      - Control operated from the outside of the housing;

      - Full voltage magnetic starters combined with fuse and fuse holder;

      - Overload protection on each phase equipped with an auxiliary contact NO and NC auxiliary contact pre-spun plate terminal identified;

      - Amperage readers with adjustable trigger points;

      - Transformer control circuit with secondary breaker;

      - Minimum timer running from 0 to 10 minutes, auxiliary pump;

      - Selector: "Manual - Off - Auto" for each pump;

      - Selector: "Drive - Workaround" for each pump;

      - Lights:

• Powered
• Walk
• Low pressure
• Overload
• Bypass Circuit

      - Automatic transfer overload;

      - Pressure switch trip point adjustable timer 0-60 seconds for the shutdown of the pumps on a low suction pressure;

      - Bypass circuit:

        - The pump system frequency will be equipped with a bypass circuit in case of failure of the drive.

        - The bypass circuit will consist of a main switch, contactors interlocked and overload protection. The components will be installed in a housing EEMAC 1

      - A variable frequency drive (VFD’S):

        - The VFD’S will be able to run the pumps to provide the lowest kilowatt use or meet the changing process parameters. This optimization requires a pressure sensor for activation. Analogue input resolution is at least 12 bits, and each analog input scan controller for a minimum of once every 100 milliseconds. All sensor inputs are individually wired to the VFD for scanning and continuous basis for comparison. All analog inputs are equipped with circuits to provide current limit protection and backup short circuit against incorrect wiring of the sensors.

        - The VFD’S will select the analog input signal that diverts the greatest amount of control point. This selected signal is used as feedback for hydraulic stabilization to reduce hunting of the checkpoint. The program will use a hydraulic stabilization function PID control: Proportional, Integral and Derivative. Values proportional, integral and derivative users will be adjustable on an infinite range. Scanning and comparing the ratio that chooses the checkpoint controls and variable signal continuous process and will automatically adjust for optimum performance. Each sensor is scanned at least once every 100 milliseconds

        - The VFD’S shall be capable of operating pumps in parallel. The pump controller will be autonomous. All messages will be in English. The following features will be provided: Hold the flaws in memory.

        - The VFD’S have a data register that will keep the last 8 faults.

        - The VFD’S shall be equipped with easy to use interface with the operator full numeric keypad membrane. The human interface panel will show the following values when tilted:

• Differential pressure in psi feedback
• Status on / off pump
•% of pump speed
• Various alarm conditions
• Diagnostic Troubleshooting
• User adjustable parameters

        - The VFD’S may incorporate memory "flash" for the economy and arrangements tailored to customer needs recharging. These field determined values will be permanently held in memory "flash" for automatic reloading values specific installation site in case of data corruption due to external disturbances. The controller will also employ a device to copy the installation of sensor

        - [The VFD’S shall be capable of communicating with the building automation system (BAS) in communications cable]

        - It will be provided with overload relay suitable for use in phase volt [____], [____], [____] Hz, and will be factory wired to the pump motors and control panel. Switches to stop the fuses will be provided with matching doors to prevent opening the electrical panel while the system is running

        - The readings will be operational status of data system for remote monitoring: The modem and optional maintenance contract for remote monitoring system available

    - The pressure sensor for measuring pressure is to type:

      - Provide and install a pressure sensor for measuring pressure and transmit the result of isolated linear 4 to 20mA for use in a system with two standard 24VDC wires. The unit should be accurate to ± 0.5% full limit sizes for ranges between 10psid 100psid and to withstand static pressures above 100psi and 500psi lines with negligible changes in performance delivery. It has a steel body with corrosion-resistant connections female 1 / 4 "NPT. The unit will withstand ambient temperatures from 0 ˚ F to 200 ˚ F and having a shroud electrical NEMA 4X

    - Butterfly valves are of type:

      - Butterfly valves with a diameter equal to or greater than DN 2 1 / 2, Model without flange, with wing

      - Compliant MSS SP 67, Class 150, Class 1 MPa type EHG, body in cast iron, stainless steel valve, stainless steel stem, EPDM seat, replaceable, lever and locking lever, control gear in, for valves with a diameter greater than DN 6.

      - Maximum service pressure: 1034 kPa (150 psi).

      - Maximum service temperature: 108°C (225°F).

      - Acceptable component: Flo Fab series BFVZ.

    - The check valves are of type:

      - Silent Check Valves

        - Valves with a diameter equal to or greater than 2-1/2 DN without flanges.

          - Class 125, Class 862 kPa (125psi), body iron or cast iron, bronze internal parts, stainless steel spring (spring, heavy duty in the case of assemblies on risers down flow).

          - Acceptable component: Flo Fab series LSDDB.

    - An automatic proportional purge detects excess temperature and allows the purging of a specified quantity of water to the drain.

    - The gauges look like:

      - Dial-type gauges 4 "(100 mm) diameter, conforming to ANSI / ASME B40.1, Grade 2A, accurate to within 1%, unless otherwise indicated.

      - The gauges have a housing and a stainless steel ring polished. The movement is also stainless steel. The needle is adjustable (adjustable micrometer)

      - These gauges are calibrated so as to operate in the center of their graduation. Normally, graduation will be combined from 0 to 690 kPa (0 to 100 psi

      - Acceptable component: Flo Fab series RFF0400LF.

    - The booster pumps will be connected to the collectors of suction and 304 stainless steel and fitted with the system controller includes a variable speed (VFD’S) and a bypass circuit to form a pumping fully autonomous pre yarn, pre adjusted and tested before shipment to the conditions specified above

    - A substantial foundation will be provided to absorb vibration and provide a solid support system. Suitable fixing bolts are embedded in concrete with sockets to allow adjustment of the bolts after the concrete has been poured. The system will be placed on this foundation, carefully levelled and the bolts tightened.

    - The capabilities of the booster group is shown in the list of equipment.

    - Acceptable components : Flo Fab series T-CPS-PSM-VFD

- PART 3 – EXECUTION

  - Installation

    - Constant pressure system will be implemented by the project contractor.

    - All wiring will be implemented by the manufacturer's instructions and codes federal, provincial and local regulations.

    - Get the manufacturer to adjust the operation of the pumps. Adjust operating pressures as indicated in the description of the equipment.

    - Ensure that the pumps run in the expected direction.

    - Install and adjust the controls.

    - The manufacturer shall provide the maintenance staff of the building instructions for operation of each pump and the system total.

  - On-site Verification

    - Check the power supply.

    - Check overload protection settings.

    - Fill pumps with liquid and jog to ensure they are rotating the proper direction.

    - Check setting and operation of the selectors' Hand-Off-Auto "and" Drive - Bypass and variable speed (VFD) bypass circuits, control devices and security alarms sound and visuals, guards against overheating and other securities

    - Set the crushers and presses - packing mounted on the shaft of the impeller.

End of Section