- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Drawings must show or indicate the following:

      - Devices and their components, including connections, piping, fittings and control devices, as well as details concerning the factory mounted or assembled on site;

      - The schematic diagrams and actual wiring;

      - Dimensions and recommended installation instructions;

      - Curves and actual performance characteristics of pumps;

    - Submit pump curves showing the operating point, for verification

    - Submit detailed wiring diagrams of control systems established by the manufacturer, indicating the wiring and equipment installed at the factory on equipment or necessary piece to controls auxiliary equipment, parts and accessories regulators

    - Shop drawings must indicate the final location during assembly on site, control devices, piping, valves and fittings shipped separately by the hardware vendor

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

  - Submersible Grinder pump to lift waste or effluent water

      - Flow : [____] L/s ([____] gal US/min);

      - Head : [____] kPa ([____] feet);

      - Discharge DN [____].

    - Pump submersible Sewage Grinder with their brand motor Flo Fab should have a capacity as indicated. The liquid will be pumping water at a maximum operating temperature of 40 º C (104 º F). The pumps must be able to handle spherical solids and the pump discharge must be a standard collar vertical positions. The double mechanical seal of the shaft must be fitted a single spring operating in a cavity filled with oil. Fins at the rear pump housing of the drive must develop a pressure differential. This pressure differential must be transmitted to the oil in the seal cavity through a rubber diaphragm, producing a higher pressure inside the cavity of the joint immediately adjacent to the face of the seal in the casing of the pump forcing oil into the cavity of the joint to lubricate seal face. The faces must be rotating carbon and ceramic faces fixed. The hardware should be stainless steel. Single phase motors in air must be protected against overload. Three-phase motors in air must also have protection against an overload in the magnetic starter.

    - Installation type a pump approved by CSA: cast iron, with open type impeller in cast iron, stainless steel shaft, mechanical double seal with shaft.

    - The set will form a compact unit including a cover adapted controls, a control panel and all useful hardware. Wiring between the panel and components will be the responsibility of the installer of pumps

    - The control panel is a NEMA-1 (USA) OR EEMAC-1 (CANADA) comprising:

      - Main switch on handle and on the door;

      - Sets of power fuses;

      - Magnetic starter with adjustable overload relay;

      - Transformer control if required with secondary fuses;

      - Operating mode selectors "Manual - Off - Auto"

      - LEDs: Power light, pump functionality light;

      - Terminal is planned for a dry contact for remote alarm;

      - Terminals for floats;

      - A visual and audible high level alarm with dry contact remote input.

    - The starting and stopping of pump will be controlled by two floats with lifts NO contacts connected to the control panel. The cables will be floats of length [20] [30] [50] feet. A third float will be used to report the highest level of well water and trigger the alarm. These floats must also be provided with a tie ribbon of stainless steel for easy installation into a moist well.

    - Order: mechanical switches and control unit for installation type one pump.

    - One elbow sets to automatic lifts for the pump Flo Fab series BAF. This includes basic and self-releasing bends between the pump and piping. Supports on top of the sump will guide for pump removal if needed.

    - Valves: The pump shall be provided with a ball check valve, branded Flo Fab series CB. Each valve must be fitted with an NPT or flanged connection, designed for vertical and horizontal installations. The check valve must be specifically designed for handling sewage or effluent. The valve design shall be such that solids, fibrous material, abrasives, rags, etc., can pass through without the need for flow-cons flush. In the operation mode, the ball must not impede flow through the valve and must prevent deadlock. The ball must be made of iron coated hollow rubber or phenolic resisting materials that are normally found in sewers. The body of the access plate shall be cast iron, ASTM Class 30 and Class 125. All fasteners must be stainless steel 18-8.

    - One chain hoist and chain hooks: Provide and install lengths of load chain with galvanized hooks suitable for lifting well pump for inspection and maintenance.

    - A tank [____] [____] mm x mm deep x mm [____] ([____] "diameter x [____]" deep x [____] "thick) fiberglass reinforced polyester resin and branded Flo Fab series FB which will be designed as submersible pump for dewatering, and effluent waters from sewage. Thickness of the wall must withstand a load of sand saturated with water of 120 psi ` and have a safety factor of 2. The support flange test must stick to at least 3’’ (76mm) radius of the basin. When the tank is securely fastened to cement slab or the clamp is covered by cement, it cannot come up or be lifted to the surface if the latter is empty because of the confining pressure. The basin is capable of withstanding a maximum temperature of 66 º C (150 º F).

    - A tank [____] [____] mm x mm deep x mm [____] ([____] "diameter x [____]" deep x [____] "thick) polyethylene brand Flo Fab series PB will be designed as submersible pumps for dewatering, effluent or waters from sewage. This tank is equipped with ultra-thick edges, to the test of cracking, and chipping; rot, of rust or corrosion. Because of its light weight, special equipment for handling isn’t required.

    - The rectangular steel lid (cover) [____] mm [____] mm length x width x ([____] [____] mm [____] inch long x "wide x [____] inch thick) or round [____] [____] mm x mm ([____] "diameter x [____] inch thick) will include a manhole, vent, and the required holes for switches floats and will have two parts. It will be covered with a coat of alkyd primer. An access cover, minimum load of 1 MPa (150 psi) and the size described in the plans must be provided by the manufacturer of pumps. The steel frame must be repressed by 6.4 mm (1/4") steel with aluminum braces where needed.

    - Solid Round Blank Steel Cover type BS

The solid Blank steel cover shall be constructed of continuous mat ASTM  Flo Fab transferred manufacturing. No less than 1/4” inch thickness. The cover shall be black in color. The cover shall be mounted to the wet well with six 3/8 inch 300 series stainless steel fasteners. The cover rating is 300 lbs per square foot.

    - Solid Round Blank Fiberglass Cover type BF-GL-FSC

The solid Blank fiberglass cover shall be constructed of continuous mat ASTM D3753-99, Flo Fab resin transferred molded manufacturing. No less than 3/8” inch thickness. The cover shall be green in color. The cover shall be mounted to the wet well with six 3/8 inch 300 series stainless steel fasteners. The cover rating is 300 lbs per square foot.

    - Solid Round Blank Checkered Cover type BCP-LB-D

The solid steel checkered cover shall be constructed of continuous mat ASTM D3753-99, Flo Fab transferred manufacturing. No less than 1/4” inch thickness. The cover shall be black in color. The cover shall be mounted to the wet well with six 3/8 inch 300 series stainless steel fasteners. The cover rating is 300 lbs per square foot.

    - Simplex Round Steel Covers type SI-LB-S-00.250

The Simplex steel cover shall be constructed to min load ratings per site engineers. Shall have either powder coated finish, enamel painted coating or epoxy painted coating.  (ASTM A 36) structural steel plate . No less than 1/4” inch thickness .The cover shall be mounted to the wet well with six 3/8” 300 series stainless steel fasteners. Pump discharge to be 2” and Vent to be 3”. The cover rating is 300 lbs per square foot.

    - Duplex Round Steel Covers type DI-LB-S-00.250

The Duplex steel cover shall be constructed to min load ratings per site engineers. Shall have either powder coated finish, enamel painted coating or epoxy painted coating. (ASTM A 36) structural steel plate. No less than 1/4” inch thickness .The cover shall be mounted to the wet well with six 3/8” 300 series stainless steel fasteners. Pump discharge to be 2” and Vent to be 3”.The cover rating is 300 lbs per square foot.

    - Simplex Round Fiberglass Hinged Door Cover type FB-SC-GL

The fiberglass hinged door, cover shall be constructed of continuous mat, (Flo Fab) resin transferred molded manufactured. No less than 3/8 inch thickness. The cover shall be green in color. The cover shall be mounted with min six 300 series stainless steel fasteners. The access hatch cover shall have a lift handle and a means of locking. The hatch shall have a positive means of holding door open in the vertical position (Locking hold open arm) made of a non- corrosive material. All hard ware shall be of 300 series stainless steel. The cover shall be mounted with minimum of six 300 series stainless steel fasteners. The cover rating is 300 lbs per square foot.

    - Duplex Round Fiberglass Hinged Door Covers type FB-DC-GL

The fiberglass hinged door, cover shall be constructed of continuous mat, (Flo Fab) resin transferred molded manufactured. No less than 3/8 inch thickness. The cover shall be green in color. The cover shall be mounted with min six 300 series stainless steel fasteners. The access hatch cover shall have a lift handle and a means of locking. The hatch shall have a positive means of holding door open in the vertical position (Locking hold open arm) made of a non- corrosive material. All hard ware shall be of 300 series stainless steel. The cover shall be mounted with minimum of six 300 series stainless steel fasteners. The cover rating is 300 lbs per square foot.

    - Simplex Round Steel Hinged Door Covers type S-SC

The Simplex Steel hinged door, cover shall be constructed of continuous material, (Flo Fab) Steel No less than 3/8 inch thickness. The cover shall be black in color. The cover shall be mounted with min six 300 series stainless steel fasteners. The access hatch cover shall have a lift handle and a means of locking. The hatch shall have a positive means of holding door open in the vertical position (Locking hold open arm) made of a non- corrosive material. All hard ware shall be of 300 series stainless steel. The cover rating is 300 lbs per square foot.

    - Duplex Round Steel Hinged Door Covers type S-DC

The Duplex Steel hinged cover shall be constructed of 3/8 inch material for wet well of diameter from 24 inch to 48 inch. Material for 60 diameters and up will be of 3/8” all conforming to (ASTM A36). The access hatch shall have a positive means of holding door open in the vertical position (Locking hold open arm) made of a non-corrosive material. All hardware shall be of 300 series stainless steel. The cover shall be mounted with minimum of six 300 series stainless steel fasteners. The cover rating is 300 lbs per square foot.

    - Steel Simplex Round Hinged Door Covers Gasket Tight type S-SC-G

The Simplex cover shall be constructed of ¼ inch material for wet well of diameter from 24 inch to 48 inch. Material for 60 diameters and up will be of 3/8” all conforming to (ASTM A36). The access hatch shall have a positive means of holding door open in the vertical position (Locking hold open arm) made of a non-corrosive material and shall be gasketed. All hardware shall be of 300 series stainless steel. The cover shall be mounted with minimum of six 300 series stainless steel fasteners.  The cover rating is 300 lbs per square foot.

    - Steel Duplex Round Hinged Door Covers Gasket Tight type S-DC-G

The Duplex cover shall be constructed of 3/8 inch material for wet well of diameter from 24 inch to 48 inch. Material for 60 diameters and up will be of 3/8” all conforming to (ASTM A36). The hatch shall have a positive means of holding door open in the vertical position (Locking hold open arm) made of a non-corrosive material and shall be gasketed. All hardware shall be of 300 series stainless steel. The cover shall be mounted with minimum of six 300 series stainless steel fasteners. The cover rating is 300 lbs per square foot.

    - Characteristics; Brand: Flo Fab:

      - Model : [____];

      - Drive [s]: [____] HP, hermetic, with protection against overloads;

      - Electricity : [____] V / [____] ph]  / [____] Hz / [____] RPM;

      - Control Panel: SSP Simplex

      - Float system: model 720163, suspended, with weight # 720149.

    - Operation sequence: SSP for Simplex  Pump should be controlled by mechanical float(s) switches for liquid level control operating through the control panel of the pump:

      - FOR SIMPLEX PUMP OPERATION

        - Float 1 (Level 1) Stop of pump

        - Float 2 (Level 2) Starts the pump

        - Float 3 (High Level 3) Audible alarm.

    - Acceptable Products: Flo Fab series S-FGC-LBV-B-BAF (for waste or effluent water).

- PART 3 – EXECUTION

  - Installation

    - In each case, doing mechanical and electrical connections between the pump, motor and control devices, as indicated.

    - Ensure that all pump motor does not support the pipe.

    - Once assembly is complete and the cover plate in place, align the entire pumping vertical submerged pump in the sump.

    - Spread a layer of sand of 150mm under the tank sump.

    - Make sure the pump runs in the expected direction.

    - The check valve and the shut off valve must be installed at the end of the vertical discharge pipe so that there is no hammer on the valve when the pump stops.

    - Install and adjust the controls.

  - Quality control on site

    - Check the power supply.

    - Check protection devices starters.

    - Start the pump and ensure it operates safely and appropriately.

    - Check setting and operation of the selector "Manual - Auto-Stop" control devices and security alarms sound and visual devices for protection against overheating and other securities.

    - Adjust the flow to water-cooled bearings.

    - Set the crushers and presses - packing mounted on the shaft of the impeller.

  - Start-up

    - According to the provisions of Section [01810 - Commissioning], in terms of general requirements and the requirements of this section.

    - Procedure:

      - Check the power supply;

      - Check the heater power overload starter;

      - Start the pump, checking the operation of the impeller;

      - Ensure that it operates safely and efficiently;

      - Check the settings and the operation of safety devices, devices for protection against overheating, audible and visual alarms and similar devices;

      - Check switch operation "Manual - Off - Auto";

      - Check the operation of the alternator.

Fin de section