- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to :

      - ANSI / ASME B16.22, Wrought Copper and Copper-Alloy Solder Joint Pressure Fittings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

  - Submittals

    - Supply the required manuals and incorporate them into an « Instruction and Maintenance Manual ».

    - The maintenance manual will comprise of or indicate the following :

      - A description of the major components; the manufacturer, a type, series or model number reference, year constructed, horsepower rating, flow and pressure.

- PART 2 – PRODUCT

  - Duplex Glycol Fill System

    - Supply and install a device to pressurize a closed loop glycol system.

    - This device will automatically replenish the loss of glycol in a closed loop system. The device’s dimension are as follows: 30" (762 mm) diameter x 71" (1804 mm) high, and will contain the following elements:

      - A  2757L (200US gal) closed polyethylene tank with cover;

      - Duplex Glycol fill system will include 2 pumping systems that are identical and independent of each other.

      - Each pumping system contains the following elements:

        - The rotary vane positive displacement pumps Series CYS shall be constructed 304 of stainless steel, and will have built-in By-Pass relief valve. These pumps shall have carbon graphite vanes, carbon rotating seal, ceramic stationary seal with Buna N bellows and stainless steel spring.

        - Motor: 1/3 HP @ 120 V / 1 ph / 60 Hz, 1750 RPM.

        - Capacity: 1 USGPM @ 100ft head.

        - Each control panel contains the following elements :

          - NEMA-1 (US) or EEMAC-1 (CANADA) enclosure;

          - Main disconnect;

          - Pilot light indicators ;

          - Low-level shut-off float;

          - System pressure switch;

          - 3 position selector switch «H-O-A»;

          - Dry contact for remote alarm signal.

        - When the pressure switch has reached its set point, the pump is shut down.

        - Adjustable pressure relief valve, with discharge piped to tank.

        - Ball valves, pressure gages and silent bronze check valves are installed on the discharge of each pump.

        - In”Auto” mode, the low-level float installed in the tank shall disable the pump should the glycol level become dangerously low.

        - In « Manual » mode, the pump can serve to replenish the system with glycol. The low-level float does not disable the pump in « Manual » mode.

      - Acceptable products: Flo Fab Series D-GLY.

- PART 3 – EXECUTION

  - Installation

    - Power wiring, as required, shall be the responsibility of the electrical contractor.  All wiring shall be performed per manufacturer’s instruction and applicable state, federal, and local codes.

    - Control wiring for remote mounted switches and sensor / transmitters shall be the responsibility of the controls contractor. All wiring shall be performed per manufacturer’s instructions and applicable state, federal, and local codes.

    - Provide drains for bases and seals, piped to and discharging into floor drains.

End of Section