- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Code of construction in Québec - Chapter 1 », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to :

      - ANSI / ASME B16.22, Wrought Copper and Copper-Alloy Solder Joint Pressure Fittings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

  - Submittals

    - Supply the required manuals and incorporate them into an « Instruction and Maintenance Manual ».

    - The maintenance manual will comprise of or indicate the following :

      - A description of the major components; the manufacturer, a type, series or model number reference, year constructed, horsepower rating, flow and pressure.

- PART 2 – PRODUCT

- Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; S-GLY,-D-GLY,-T-GLY,-Q-GLY or comparable product by the following:

  - Glycol Fill System

The rotary vane positive displacement pump(s) series CYS shall be constructed 304 of stainless steel, and will have built-in By-Pass relief valve(s). The pump(s) shall have carbon graphite vanes, carbon rotating seal, ceramic stationary seal with Buna N bellows and stainless steel spring.

Pumps:

- Type: [Rotary vane glycol handling Flo Fab Select Series] <Insert pump designation> as defined in centrifugal pumps above

- Mounting: Horizontal type

- Number of Pumps: [one] [Two] [Three] [four] <Insert Number>.

    - Supply and install a device to pressurize a closed loop glycol system.

    - This device will automatically replenish the loss of glycol in a closed loop system. The device’s dimension are as follows:

Select Required Tank

      - A ECONO (53US gal) 22” (553 mm) x 39” (990 mm) (closed polyethylene tank with cover;

      - B  (25 US gal) 18” (457mm) x 28” (737mm closed polyethylene tank with cover;

      - C (53 US gal) 22” (559 mm) x 39” (990 mm) closed polyethylene tank with cover;

      - D (100 US gal) 30” (762 mm) x 43” (1092 mm) closed polyethylene tank with cover;

      - E (200 US gal) 30” (762 mm) x 87” (2210 mm)closed polyethylene tank with cover;

      - The pumping system contains the following elements:

      - See Pump schedule for details

        - Capacities and Characteristics

        - Motor: __ HP @ Volts: [120] [240] [208] [380] [460] [575]

        - Pump Capacity: ___ USGPM @ ________ head

        - Each control panel contains the following elements :

          - NEMA-1 (US) or EEMAC-1 (CANADA) enclosure;

          - Main disconnect;

          - Pilot light indicators ;

          - Low-level shut-off float;

          - System pressure switch;

          - 3 position selector switch «H-O-A»;

          - Dry contact for remote alarm signal.

        - When the pressure switch has reached its set point, the pump is shut down.

        - Adjustable pressure relief valve, with discharge piped to tank.

        - Shut Off Valves:

          - Bronze Ball Valves, Two-Piece with Full Port and Stainless-Steel Trim:

            - Standard: MSS SP-110.

            - SWP Rating: 150 psig (1035 kPa).

            - CWP Rating: 600 psig (4140 kPa).

            - Body Design: Two piece.

            - Body Material: Bronze.

            - Ends: Threaded.

            - Seats: PTFE.

            - Stem: Stainless steel.

            - Ball: Stainless steel, vented.

            - Port: Full

          - Bronze Lift Check Valves with Bronze Disc, Class 125:

            - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Series STB or comparable product by the following:

            - Standard: MSS SP-80, Type 1.

            - CWP Rating: 200 psig (1380 kPa).

            - Body Design: Vertical flow.

            - Body Material: ASTM B 61 or ASTM B 62, bronze.

            - Ends: Threaded.

            - Disc: Bronze.

        - Ball valves, pressure gages and silent bronze check valves are installed on the discharge of each pump.

        - In ”Auto” mode, the low-level float installed in the tank shall disable the pump should the glycol level become dangerously low.

        - In « Manual » mode, the pump can serve to replenish the system with glycol. The low-level float does not disable the pump in « Manual » mode.

- PART 3 – EXECUTION

  - Installation

    - Power wiring, as required, shall be the responsibility of the electrical contractor.  All wiring shall be performed per manufacturer’s instruction and applicable state, federal, and local codes.

    - Control wiring for remote mounted switches and sensor / transmitters shall be the responsibility of the controls contractor. All wiring shall be performed per manufacturer’s instructions and applicable state, federal, and local codes.

    - Provide drains for bases and seals, piped to and discharging into floor drains.

    - Glycol Fill System Operation and Sequencing:

    - When the pressure switch has reached its set point, the pump is shut down.

    - Adjustable pressure relief valve, with discharge piped to tank.

    - Ball valves, pressure gages and silent bronze check valves are installed on the discharge of each pump.

    - A separate external relief valve to return the glycol solution to the holding tank.

    - In "Auto" mode, the low-level float installed in the tank shall disable the pump should the glycol level become dangerously low.

    - In "Manual" mode, the pump can serve to replenish the system with glycol. The low-level float does not disable the pump in "Manual" mode.

End of Section