- PART 1 – GENERAL

  - References

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / API 609, Lug and Wafer Type Butterfly Valves.

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Buttwelding Fittings.

      - ANSI / ASME B16.18, Cast Copper Alloy Solder Joint Pressure Fittings.

      - ANSI / ASME B16.22, Wrought Copper and Copper-Alloy Solder Joint Pressure Fittings.

      - ANSI / ASME B16.25, Butt welding Ends.

      - ANSI / ASME B16.34, Valves – Flanged, Threaded and Welding Ends.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / ASME B40.1, Pressure Gauges and Gauge attachments.

      - ANSI / ASME B40.2, Thermometers, Direct reading and Remote Reading.

      - ANSI / ASME Section VIII, Boiler and Pressure Vessel Code.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A126, Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings.

      - ASTM A167, Specification for Stainless and Heat-Resisting Chromium Nickel Steel Plate, Sheet and Strip.

      - ASTM A216 / A216M, Specification for Steel Castings, Carbon, Suitable for Fusion Welding for High-Temperature Service.

      - ASTM A276, Specification for Stainless and Heat-Resisting Steel Bars and Shapes.

      - ASTM A278, Specification for Grey Iron Castings for Pressure - Containing Parts for Temperatures up to 345C.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM A351 / A351M, Specification for Steel Castings, Austenitic, for High-Temperature Service.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CAN / CGSB-14.4, Thermometers, Liquid-in-Glass, Self-Indicating, Commercial/Industrial Type.

      - CAN / CGSB-14.5, Thermometers, Liquid-in-Glass, Self-Indicating, Commercial / Industrial Type.

      - CSA B51, Boiler, Pressure Vessel, and Pressure Piping Code.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

      - CSA W47.1S1, Supplement No 1, Steel Fixed Offshore Structures, to W47.1.

      - MSS-SP-67, Butterfly Valves.

  - Submittals

    - Submit dimensional drawings and technical data in conformance with client’s instructions.

    - Submit pump curves showing the operating point, for verification.

    - Submit detailed wiring diagrams of control systems established by the manufacturer.

    - Submit heat exchanger performance conditions and other technical information.

  - Instruction and Maintenance Manual

    - Supply the required manuals and incorporate them into an “Instruction and Maintenance Manual”.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure and/or capacity in BTU/h;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

  - Heating and Cooling Systems

    - Module HC will be composed of one pump, control panel, expansion tank, air separator, chemicals pot feeder, and glycol fill system (optional), balancing valve, isolation valves, air vents and drain connections, multifunction valve, suction diffuser or Y strainer, interconnecting black steel schedule 40 piping.  All package components are mounted on a structural steel base with lifting lugs.

    - Pre-assembling, testing and final adjusting at the factory, allows the module will be on-site ready for mechanical and electrical system connections.

  - Components included:

    - Horizontal End Suction Pumps

      - Pump Flo Fab series 1000 are stand alone closed coupled pumps, single stage, with end suction volute that can be supported.  Servicing of the pump can be performed without disturbing the piping connections.

      - Volute: Cast Iron Class 30 (ASTM No. A 159) without foot support. Threaded connections for a pressure gauge at the discharge end, as well as for venting and draining. The volute will be provided with a replaceable wear ring.

      - Impeller: Cast Bronze (ASTM No. B 584), closed type, dynamically balanced, keyed to the stainless steel shaft and secured by a stainless steel bolt and washer.

      - Coupling: No coupling design, impeller is directly coupled to the motor shaft.

      - The wet-end components are sealed with a self-lubricating mechanical seal. The seal is composed of a ceramic seat, a rotating carbon ring, a viton bellow and all other materials in stainless steel. It is designed for continuous operation at maximum working temperature of 400°F (205°C) corresponding to a maximum working pressure of 1724 kPa (250 psi). A replaceable bronze sleeve installed on the pump shaft, to protect the shaft from undue wear by the mechanical seal.

      - Pump designed for an operating pressure of [1200 kPa (175 psi)] [1724 kPa (250 psi)] [2068 kPa (300 psi)].

      - Motor: respecting the requirements of Section 15010, NEMA specifications, closed type, high efficiency, and foot mounted.

      - Selection of motor will allow the pump to operate at maximum capacity without surpassing the maximum amperage draw on the motor.

      - Each pump is hydrostatically tested.

      - Size and Capacity: As specified on pump tables shown on [plans] [specifications].

      - Acceptable component: Flo Fab series 1000.

  - Replaceable bladder expansion tank

    - [Horizontal] [Vertical] Cylindrical expansion tank with replaceable bladder.

    - Full acceptance volume: As indicated on the expansion tank table.

    - Bladder is able to resist temperatures up to 115°C (240°F).

      - BUTYL, compatible with water or ethylene-glycol.

      - EPDM, compatible to propylene glycol.

    - Design pressure: 862 kPa (125 psi) for tanks constructed in accordance with the ASME, Section VIII, Div. 1 and thus will be stamped with the ASME Logo.

    - Pre-Charge : Initial system air pressure:

      - For Heating/Cooling systems: pre-charge is equal to the fill system.

      - Description:
Capacity:       [____] L ([____] gal US)
Dimension: [____] mm Diameter x [____] mm High.
Dimension: [____] in Diameter x [____] in High.

    - [Horizontal saddle] [Vertical base].

    - Approved model :

      - Flo Fab models BT for hydronic heating and/or cooling systems incorporating steel connection.

    - Air Separator or Air/Dirt Air Separator

    - The design and fabrication will conform to ASME Section VIII Division 1 and CSA B51 relating to pressure vessels used at 150 psi (1034 kPa) and 550 ° F (288 ° C) maximum.

    - The inlet and outlet of each vessel will be equipped with an aperture of [____] inch ([____] mm) [Flanged].

    - The vessels will be equipped with separated superior NPT connector(s) for evacuation of air and lower connector(s) for other connections, such as components of pressure control (CPC).

      - The air separator shall also be supplied with automatic ¾” npt air vent model MV150-075

    - Flo Fab series SEP (Suffix F flange) (suffix G for Grooved) (Suffix L with mounting brackets) and / or (Suffix F-4 stainless steel screen 304) (Suffix F-6 stainless steel screen 316).

      - Acceptable Components: Flo Fab series SEP-.(air separator)

      - Acceptable Components: Flo Fab series ADSF-.(air/dirt  separator)

    - Water Make-up Line

    - ¾” make-up water system shall be provided. This system shall include a pressure reducing valve set at specific pressure. The valve shall include a shut-off valve, y strainer, pressure gauge and manual by-pass.

    - Chemical Pot Feeder:

      - A chemical holding tank that is pressurized by the discharge header and will release chemicals into the suction header. A maximum operating pressure of 2068 kPa (300 psi) and temperature to 93ºC (200ºF).

    - Control Panel model SP for simplex system will consist of:

      - NEMA-1 (US) or EEMAC-1 (CANADA) enclosure;

      - Main disconnect;

      - Magnetic starter combined with fuses and fuse holders;

      - Overload protection on each phase equipped with an auxiliary contact NO and NC auxiliary contact;

      - Adjustable overload protection;

      - Secondary transformer circuit breakers;

      - 3 position selector switch «H-O-A» for this pump;

      - Pilot light indicators:

          - Power on

          - Run

          - Low Pressure

          - Surcharge

      - Adjustable low suction pressure switch to stop pump.

    - Balancing Valve:

      - Globe valve inclined “Y” body, designed to allow pressure measurements and to ensure a precise regulation of flow. Pressure tapings are located at the inlet and exit of the valve to receive a differential pressure gauge.

      - Precision: The measured and displayed flow is within 25% of actual flow.

      - Diameters less than or equal to DN 2.

        - Dezincification resistant brass body, solder or sweat end connections, EPDM seat ring and dezincification resistant brass plug, and screw in bonnet, which can withstand a maximum working pressure of 1.7 MPa (250 psi) and a maximum service temperature of 121C (250F).

        - Flow regulation: Minimum 4 complete turns of the handwheel with visual dial indicator and built-in memory stopper.

      - Diameters equal or greater than DN 2 ½.

        - Epoxy coated cast iron body; all wetted brass parts shall be alloyed to resist dezincification. Grooved to 300lbs or flanged to 125lbs ANSI standard connections which can withstand a maximum working pressure of 1.7 MPa (250 psi) and a maximum service temperature of 121C (250F).

        - Flow regulation: Minimum 8 complete turns of the handwheel with visual dial indicator and built-in memory stopper.

      - Acceptable Components:

        - Globe Valve: Flo Fab series LGS or LGSS.

        - Grooved Globe Valve: Flo Fab series LGSG.

    - Suction Diffuser:

      - Cast iron construction Class 125. Maximum working pressure 1207 kPa (175 psi) and maximum working temperature 121C (250F).

      - Connection: Flanged Rating Class 125 ANSI flat face.

      - Suction Diffuser is a combination flow straightener and strainer. Strainer portion is composed of a “Start-up” mesh and permanent cylindrical sieve. Adjustable foot mounted support.

        - “Start-Up” Sieve: 20 screen mesh.

        - Permanent Sieve: Stainless Steel cylinder perforated with 3/16" (4.76 mm) holes.

      - All suction diffusers are designed to withstand a differential pressure equal to the maximum head of the pumping system at no flow.

      - The length of the flow straightening vanes will not be less than twice the diameter opening of the discharge flange connection.

      - Flow and size: according to the pump tables on [piping schematics] [specifications].

      - Acceptable Components: Flo Fab series ASDFF.

    - Butterfly Valves:

      - Butterfly valves 2” to 24”, lugged type.

      - The valves shall be of heavy-duty cast iron construction suitable for standard ANSI connections. Construction of the shaft will be in 316 stainless steel and disc in 304SS with seat in EPDM. Valve sizes 6” shall have memory stopper with set screw.

      - Maximum working pressure: 1034 kPa (150 psi).

      - Maximum working temperature: 108°C (225°F).

      - Acceptable Components: Flo Fab series LBFVZ.

    - Check Valve:

      - Check valve equal to or smaller than DN 2 (Threaded Ends).

        - Bronze Body conforms to standard ASTM B62, class 125, category 862 kPa (125 psi), brass disc and seating ring, extra robust return stainless steel spring in case of application in vertical piping).

        - Acceptable Components: Flo Fab series STB.

      - Check valves equal to or larger than DN 2-1/2 (Wafer).

        - Cast Iron or forge steel body, class 125, category 862 kPa (125 psi), bronze disc, extra robust stainless steel springs in case of application in vertical piping, and EPDM body seat for sealing.

        - Acceptable Components: Flo Fab series LSDDB.

    - Multi-function valve straight pattern

      - Diameters equal or greater than DN 2.

        - Epoxy coated cast iron body; all wetted brass parts shall be allowed to resist dezincification. Grooved to 300lbs or flanged to 150lbs ANSI standard connections which can withstand a maximum working pressure of 1.7 MPa (250 psi) and a maximum service temperature of 121°C (250°F).

        - Each valve shall have a combination of three functions flow balancing, check, and shut off, with manual hand wheel adjustment and nameplate percentage reading.

      - Acceptable Components:

        - Globe Valve: Flo Fab series MFV

    - Thermometers:

      - Direct reading industrial thermometers, adjustable reading angle, liquid filled, 9” (230 mm) scale length, in accordance with CAN / CGSB-14.4.

      - Body is a rigid aluminum rectangular frame fitted with shatterproof plexiglass window. Red mercury and adjustable angle of tube lens allows easier legibility at a distance. Bonze base that can be easily inserted and secured into a thermowell.

      - Thermometers have a combined graduation (ºC and ºF). The scaling are as follows:

        - Cooling water: -17 à 49C (0 à 120F);

        - Domestic water: 0 à 80C (32 à 180F);

        - Low Temperature Hot water: 0 à 80C (32 à 180F);

        - Standard Temperature Hot Water: 0 à 115C (30 à 240F).

      - Acceptable Components: Flo Fab series L9VU.

    - Pressure Gauges:

      - Dial indicator type with 4-1/2" (114 mm) diameter dial face.  Conforming to ANSI / ASME B40.1, Class 2A, accurate to within 1%, unless otherwise indicated.

      - Gage housing and ring is constructed of polished stainless steel.  Internal working mechanism constructed of stainless steel. Gage can be recalibrated.

      - Choose gauges with the consideration of the range and graduation of pressures to be measured, ensuring that the nominal pressure is close as possible to the center of this range.

      - Each gage must have an isolation ball valve installed at the inlet of the gage. Glycerin filled gages are to be used at the pump suction and discharge as well as in areas where there is excessive pulsations.

      - Acceptable Components: Flo Fab series RFF0400LF.

    - An automatic purge will detect excess temperature and allow the purging of a specified quantity of water to the drain.

    - Pump, control panel and all other accessories will be piped, fitted and electrically wired together and then shall go through mechanical, electrical and hydrostatic verification before shipment.

    - A solid foundation will be provided to absorb any vibration and provide a firm support system. The bolts will be embedded in the concrete with sockets to allow the adjustment of bolts after the concrete has been poured. The system will be placed on this foundation, carefully levelled and bolted down.

    - Size and Capacity: As specified on pump tables shown on plans and the specifications.

    - Pump sequencing (Simplex).

      - The sequence is as follows:

        - The P1 will run continuously. The pump can be controlled manually.

Optional Equipment

    - Glycol Fill System Flo Fab series S-GLY:

      - Supply and install a device to pressurized closed loop glycol system.  The device’s dimension are as follows: 22" (559 mm) diameter x 39" (990 mm) high, and will contain the following elements:

        - A  200L (53US gal) closed polyethylene tank with cover;

        - 304 Stainless Steel rotary vane type pump with electric closed couple motor and graphite bearings.

          - Motor: 1/3HP / 120V / 1ph / 60Hz / 1750rpm.

          - Capacity: [____] L/h ([____] gal US/min)

          - Pressure: [____] kPa ([____] psi).

        - Control panel contains the following elements:

          - NEMA-1 (US) or EEMAC-1 (CANADA) enclosure;

          - Main disconnect;

          - low-level indicator light;

          - low-level shut-off float;

          - Dry contact for remote low level alarm signal (5 Amps);

          - 3 position selector switch «H-O-A».

        - When the pressure switch has reached its set point, the pump is shut down.

        - Adjustable pressure relief valve, with discharge piped to tank.

        - Ball valves, pressure gages and silent bronze check valves are installed on the discharge of each pump.

        - A separate external relief valve to return the glycol solution to the holding tank.

        - In ”Auto” mode, the low-level float installed in the tank shall disable the pump should the glycol level become dangerously low.

        - In “Manual” mode, the pump can serve to replenish the system with glycol. The low-level float does not disable the pump in « Manual » mode.

Optional Equipment

    - Flexible Rubber Connectors

      - Maximum working pressure: 1475 kPa (214 psi).

      - Maximum working temperature: 115°C (240°F).

      - Free form or constrained, standard flexibility or extra flexibility, without packing, maintenance free, factory-tested at a pressure equal to 1-1/2 times the maximum working pressure. Test certificates can be provided.

      - Body: Material to be EPDM. High pressure moulding of single or multiple bellows.

      - Connection:

        - Smaller sizes ½” to 2”: #150 MI union fittings at both ends;

        - Larger sizes 1-½” to 20”: Floating metallic flanges designed to mate with standard 150# ANSI flanges.

      - Control Units (Optional): Protect flexible connector from excessive deformation.

        - Double Control rod plates, nickel iron;

          - Multiple control rods between control plates, carbon steel, painted.

      - Acceptable Components: Flo Fab series DUT or DSP.

    - Braided Metal Flexible Connectors

      - Interior component consist of a stainless steel accordion tube.

      - Exterior sheathing consists of a stainless steel braided mesh.

      - Diameter and end connections: as indicated on drawings.

      - Maximum working pressure: 1034 kPa (150 psi)

      - Maximum working temperature: 93°C (200°F).

      - Acceptable component:

        - 2”  and less: Flo Fab series ST;

        - 2-1/2” and larger: Flo Fab series SM.

    - Framing:

      - The frame shall be heavy-duty channel and angle iron construction. The frame and support member materials shall be ASTM 36 structural steel, all welding for the frame and piping shall be performed in accordance to ASME Section IX certified welders with certificates provided upon request.

    - Paint:

      - All Piping, steel bases and enclosure floors and exteriors are to be factory painted.

    - Product:

      - The paint shall be enamel that produces a durable chemically resistant coating. All surfaces shall be prepared with zero induction epoxy primer before applying the blue paint.

    - Acceptable System:

      - Flo Fab series S-HC-1000-SP

- PART 3 – EXECUTION

  - Installation

    - The Heat and Cooling Module is to be installed by the contractor.

    - Power wiring, as required, shall be the responsibility of the electrical contractor.  All wiring shall be performed per manufacturer’s instruction and applicable state, federal, and local codes.

    - Pipe work and connections:

      - When connecting pipe to installed equipment connect pipe in accordance with the manufacturer’s instructions. Use valves and flanges for isolation and ease of maintenance and assembly. Provide recommended clearances around all systems, equipment and component as recommended by the manufacturer. Install piping to facilitate drainage and/or condensate management. Install drain valves at low points in the piping systems, at equipment and at section isolating valves, Provide drain valves at each drain locator. Drain valves shall have cap and chain and to be minimum ¾ “npt.

    - Control wiring for remote mounted switches and sensor / transmitters shall be the responsibility of the controls contractor. All wiring shall be performed per manufacturer’s instructions and applicable state, federal, and local codes.

    - Install support elements or piping hangers such that the body of the connecting flanges of the module does not support the any piping or equipment. Refer to details and installation instructions from the manufacturer.

    - Provide drains for bases and seals, piped to and discharging into floor drains.

    - Jog pump and verify that the fluid flows in the direction indicated by the arrow engraved on the body, that grease nipples are easily accessible and once power is applied to the motor that the impeller in rotating in the correct direction.

    - The manufacturer shall provide the maintenance staff of the building instructions for operation of each pump and the system total.

  - On-site Verification

    - Check the power supply.

    - Check overload protection settings.

    - Fill pump with liquid and jog to ensure they are rotating the proper direction.

    - Check settings and operation of selectors "Manual-Off-Auto", control devices, security alarm sounds and other devices for protection against overheating and overpressure.

End of Section