Copyright 2013 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Product MasterSpec Section is licensed by ARCOM to Flo Fab Inc. ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text, and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, ARCOM or The American Institute of Architects (AIA).  Neither AIA nor ARCOM are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user.  A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Flo Fab Inc., 860 Industrial Boulevard, Bois-des-Filion, QC J6Z 4V7; Phone: +1 450-621-2995; Fax +1 450-621-4995; Website: www.flofab.com; Email: salesteam@flofab.com.

For information about MasterSpec contact ARCOM at (800) 424-5080 or visit www.MasterSpec.com.

SECTION 232123 - HYDRONIC PUMPS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Close-coupled, in-line centrifugal pumps.

          - Close-coupled, end-suction centrifugal pumps.

          - Separately coupled, horizontally mounted, in-line centrifugal pumps.

          - Separately coupled, vertically mounted, in-line centrifugal pumps.

          - Separately coupled, base-mounted, end-suction centrifugal pumps.

          - Separately coupled, base-mounted, double-suction centrifugal pumps.

          - Separately coupled, vertically mounted, double-suction centrifugal pumps.

          - Separately coupled, vertically mounted, turbine centrifugal pumps.

          - Wet-rotor pumps.

          - Modular packaged pump systems.

          - Automatic condensate pump units.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - Buna-N: Nitrile rubber.

        - EPT: Ethylene propylene terpolymer.

        - NPSH: Net positive suction head.

        - VFC: Variable-frequency controller(s).

      - ACTION SUBMITTALS

        - Product Data: For each type of product indicated.

          - Include certified performance curves and rated capacities, operating characteristics, furnished specialties, electrical characteristics, and accessories for each type of product indicated.

          - Indicate pump's final impeller dimensions, and operating point on curves.

        - Shop Drawings: For each product indicated.  For pump packages include plans, elevations, sections, details, and attachments to other work.

          - Show pump layout, component layout and connections.

          - Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, model numbers, and location and size of each field connection.

          - Wiring Diagrams: For power, signal, and control wiring.

      - INFORMATIONAL SUBMITTALS

Retain "Performance Tests" paragraph below if retaining certification in "Quality Assurance" Article.

        - Performance Tests: For optional production performance tests in "Quality Assurance" Article.

        - Field Quality-Control Reports: Startup service reports.

        - Sample Warranty: For manufacturer's warranty.

      - CLOSEOUT SUBMITTALS

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Operation and Maintenance Data: For pumps to include in emergency, operation, and maintenance manuals.

          - Exploded view diagrams with component parts list.

          - Instructions for installation, start-up, and operation.

          - Description of maintenance and care procedures.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise "Mechanical seals", "Bearing sets" and "Couplings" Subparagraphs below to suit Project.

          - Mechanical seals: [One] <Insert number> mechanical seal(s) for each pump.

          - Bearing sets: [One] <Insert number> bearing set(s) for each pump.

          - Couplings: [One] <Insert number> coupling(s) for each pump.

      - QUALITY ASSURANCE

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain the following paragraph for optional acceptance tests by the manufacturer.  See the following website link for test details:

http://www.flofab.com/HomeSite/Literature/Documents/Certificates/Hydraulic%20Performance%20Tolerence/Brochure/en/?SessionNoClient=1347&SessionAdministrator=0

        - Production Performance Acceptance Tests:

          - ANSI/HI 14.6, Hydraulic Institute Performance Acceptance Tests: Five test points at levels 2B, 2U, or 3B.

          - Certified NPSH curve.

          - Factory witness test.

          - Certified motor test.

        - ASME Compliance:

          - ANSI/ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

          - ANSI/ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

          - ANSI/ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

          - ANSI/ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

          - ANSI/ASME B18.2.1, Square and Hex Bolts and Screws.

          - ANSI/ASME B18.2.2, Square and Hex Nuts.

        - ASTM Compliance:

          - ASTM A47 / A47M, Specification for Ferritic Malleable Iron Castings.

          - ASTM A48 / A48M, Standard Specification for Gray Iron Castings.

          - ASTM A53 / A53M, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

          - ASTM A536, Specification for Ductile Iron Castings.

          - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

          - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

        - AWWA Compliance:

          - ANSI/AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

        - CSA Compliance:

          - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

          - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

      - WARRANTY

Visit the website for a copy of the warranty and exclusions:

http://www.flofab.com/HomeSite/Literature/Documents/ARRA,%20Terms%20and%20conditions/Terms%20and%20Conditions/Brochure/en/Flo%20Fab%20Standard%20Terms%20and%20Conditions%20of%20Sale%20US%2011%20March,16.pdf

- Manufacturer's Warranty: Manufacturer undertakes during the period of warranty to
repair or to replace with new, in the shortest time possible, any parts found to present recognized defects in materials, construction or workmanship that render them unfit for the intended use.  The warranty on the products has the following duration from the date of shipping the material to job site:

          - Pumps: 5 years.

          - Packaged Systems: 8 years.

      - DELIVERY, STORAGE, AND HANDLING

        - Retain protective coatings and flange's protective covers during storage.

      - COORDINATION

        - Coordinate sizes and locations of concrete bases with actual equipment provided.

- PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

      - CLOSE-COUPLED, IN-LINE CENTRIFUGAL PUMPS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; 600/880 Series or comparable product by one of the following:

          - Crane Pumps & Systems.

          - ITT Corporation.

          - KUBOTA Corporation.

          - Mepco, LLC.

          - Naniwa Pump Mfg Co., Ltd.

          - Peerless Pump Company.

          - Thrush Co. Inc.

        - Description: Factory-assembled and -tested, centrifugal, overhung-impeller, close-coupled, in-line pump as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted horizontally or vertically.

The Flo Fab close-coupled, in-line pump is fully serviceable at site without disturbing the piping connections.  Flo Fab pitot tube flow meters can be supplied and installed on the discharge of the volute casing for taking differential pressure readings and confirming pump capacity.  Incorporated in the volute casing is a solid base with four anchor holes and a connection to drain that can accommodate a valve with bronze cap.

        - Pump Construction:

          - Casing: ASTM A48, Class 30, cast iron, suction and discharge flanged connections [Class 125][Class 250], with threaded gage tappings at inlet and outlet, replaceable wear rings, and a solid base with four anchor holes.

          - Impeller: One-piece enclosed type corrosion resistant Noryl, closed type; statically and dynamically balanced, keyed to shaft, and secured with a stainless steel bolt and washer. For constant-speed pumps, trim impeller to match specified performance.

For easy service on site and to avoid vibrations and high failure rates, pumps with shafts supported by the motor bearings are not allowed.  Pump design should allow easy and quick removal and service of impeller and seal.  Automatic Purge System: Liquid flows from the high pressure side of the impeller across the seal face to the low pressure eye of the impeller and assures proper lubrication and venting.

          - Pump Shaft:  Stainless steel, fitted with bronze sleeve and Buna-N O-ring.

In "Mechanical Seal" subparagraph below, mechanical seal is suitable for service temperatures above 250 deg F (121 deg C). The "Viton" bellow is for a maximum working temperature of 300 deg F (149 deg C), a maximum working pressure of 250 psig (1724 kPa).  Optional: Maximum working temperature of 400 deg F (205 deg C), a maximum working pressure of 250 psig (1724 kPa), and for glycol solutions.

          - Mechanical Seal: Self-lubricating mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Viton bellows and gasket.

          - Coupling:  No coupling design.  Pump impeller directly connected to the motor shaft.

        - Motor: Single speed and rigidly mounted to pump casing, close coupled-pump motor, JM motor type.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

            - Motor Bearings:  Grease-lubricated ball bearings.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient<, inverter-duty> <Insert designation>.

            - NEMA Design: B <Insert designation>.

            - Service Factor: 1.15 <Insert value>.

        - Accessories:

          - Flow Meter: Pitot tube flow meter for field installation on the casing discharge, model [FMI] <Insert designation>.

          - Casing Drain Valve: Drain valve with bronze cap for field installation on the casing discharge, model [HN0050] <Insert designation>.

If Project has more than one type or configuration of close-coupled, in-line centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

Select motors to allow the pump to operate at maximum capacity without surpassing the amperage draw.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1720 kPa)].

          - Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)].

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: [120] [240] [208] [380] [460] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: [60] [50].

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - CLOSE-COUPLED, END-SUCTION CENTRIFUGAL PUMPS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; 1000/1004 Series or comparable product by one of the following:

          - Buffalo Pumps, Inc.

          - Crane Pumps & Systems.

          - Flowserve Corporation.

          - ITT Corporation.

          - Mepco, LLC.

          - Peerless Pump Company.

          - Thrush Co. Inc.

        - Description: Factory-assembled and -tested, centrifugal, overhung-impeller, single-stage, close-coupled, end-suction pump as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted horizontally.

The Flo Fab close-coupled, end-suction pump is fully serviceable at site without disturbing the piping connections.

        - Pump Construction:

          - Casing: ASTM A48, Class 30, [cast iron] [cast bronze], without foot support, with replaceable bronze wear rings, drain plug at bottom and air vent at top of volute, threaded gage tappings at outlet, and [threaded companion-flange] [flanged] connections.

In subparagraph below, 8-bladed impeller improves flow hydraulics, stabilizes flow and reduces turbulence. Manufactured by vacuum-cast foundry process that provides smooth waterways and dimensional control not found in sand casting.

          - Impeller: ASTM B 584, [cast bronze] [cast iron], vacuum-cast foundry process, closed type; eight-bladed, statically and dynamically balanced, keyed to shaft, and secured with a stainless steel bolt and washer. For constant-speed pumps, trim impeller to match specified performance.

In subparagraph below, carbon steel clip-fitted, pin-locked bronze shaft sleeve extending through seal box prevents shaft wear and corrosion.  Elastomer gaskets seal both the shaft sleeve and the impeller cap screw to prevent shaft corrosion and isolate shaft from pumped liquid.

          - Pump Shaft: Carbon steel slip-fitted, pin-locked bronze shaft sleeve extending through seal box.  Elastomer gaskets to seal both the shaft sleeve and the impeller cap screw.

In "Mechanical Seal" subparagraph below, mechanical seal is suitable for service temperatures above 250 deg F (121 deg C). The "Viton" bellow is for a maximum working temperature of 300 deg F (149 deg C), a maximum working pressure of 250 psig (1724 kPa).  Optional: Maximum working temperature of 400 deg F (205 deg C), a maximum working pressure of 250 psig (1724 kPa), and for glycol solutions.

          - Mechanical Seal: Self-lubricating mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Viton bellows and gasket.

          - Coupling:  No coupling design.  Pump impeller directly connected to the motor shaft.

        - Motor: Single speed and rigidly mounted to pump casing with integral pump support, close coupled-pump motor, JM motor type.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: Cast iron.

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

            - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient<, inverter-duty> <Insert designation>.

            - NEMA Design: B <Insert designation>.

            - Service Factor: 1.15 <Insert value>.

        - Accessories:

          - Flow Meter: Pitot tube flow meter for field installation on the casing discharge, model [FMI] <Insert designation>.

          - Casing Drain Valve: Drain valve with bronze cap for field installation on the casing discharge, model [HN0050] <Insert designation>.

If Project has more than one type or configuration of close-coupled, end-suction centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

Select motors to allow the pump to operate at maximum capacity without surpassing the amperage draw.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1724 kPa)] [300 psig (2068 kPa)].

          - Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)] [400 deg F (205 deg C)].

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: [120] [240] [208] [380] [460] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: [60] [50].

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - CENTRIFUGAL PUMPS WITH UNIVERSAL CASINGS

Flo Fab centrifugal pumps are available in multiple suction and discharge configurations for vertical or horizontal orientation.  Select from the subparagraphs below.  See website for catalog.

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; XRI multi position pump or comparable product by one of the following:

          - ITT Corporation.

          - KUBOTA Corporation.

          - Mepco, LLC.

          - Naniwa Pump Mfg Co., Ltd.

          - PACO Pumps; Grundfos Pumps Corporation, USA.

          - Peerless Pump Company.

          - Scot Pump; a division of Ardox Corporation.

          - Thrush Co. Inc.

        - Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, end-suction pump as defined in HI 1.1-1.2 and HI 1.3; designed for base mounting, with pump and motor shafts horizontal.

Universal XRI pump configurations are Crossed Vertical (CV), Inline Vertical (IV), L-Shaped Vertical (LV), U-Shaped Vertical (UV), End Suction Top Horizontal (ETH), End Suction Horizontal (ESH), Inline Horizontal (IH), U-Shaped Horizontal (UH), Crossed Horizontal (CH), L-Shaped Horizontal (LH).

Edit the pump construction subparagraphs below and then choose either the vertical or horizontal pump configuration.

        - Pump Configuration:

          - Vertical position with discharge casing and suction casing. <Provide volute casing base with anchor holes.>

            - <Crossed Vertical (CV)> <Inline Vertical (IV)> <L-Shaped Vertical (LV)> <U-Shaped Vertical (UV)>.

          - Horizontal position with discharge casing and suction casing. <Provide volute casing base with anchor holes.>

            - <End Suction Top Horizontal (ETH)> <End Suction Horizontal (ESH)> <Inline Horizontal (IH)> <U-Shaped Horizontal (UH)> <Crossed Horizontal (CH)> <L-Shaped Horizontal (LH)>.

        - Pump Construction:

Not all manufacturers provide volute supports that allow removal and replacement of impeller without disconnecting piping.

The Flo Fab pump is a back-pullout design, fully serviceable at site by removing the impeller housing which includes impeller, bearings, and mechanical seal in vertical or horizontal positions, without disturbing the piping connections or removing the motor.  All bearings an integral part of the impeller housing.

For easy service on site and to avoid vibrations and high failure rates pumps with shafts supported by the motor bearings are not allowed, to ensure total cost of ownership and quick economical operational life all pumps to be supplied with standard generic motors, seals and bearings, pumps with proprietary or exclusive motors, seals or bearings are not allowed.

For durability pump should be supplied with both casing and impeller wearing rings.

          - Casing: ASTM A48, Class 30, cast iron, with replaceable bronze wear rings on casing and impeller, threaded gage tappings at inlet and outlet, drain plug at bottom and air vent at top of volute, and [threaded companion-flange] [flanged] connections.[ For vertical installation, provide solid volute casing base with four anchor holes.][ For horizontal  installation, provide casing and motor steel base plate.]

          - Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, keyed to shaft, and secured with a stainless steel bolt and washer. For pumps not frequency-drive controlled, trim impeller to match specified performance.

To avoid vibrations and high failure rates, do not allow pumps with shafts supported by the motor bearings.

          - Pump Shaft:  Stainless steel, fitted with bronze sleeve and Buna-N O-ring.

Mechanical seal is suitable for service temperatures above 200 deg F (93 deg C). The "Viton" bellow is for a maximum working temperature of 400 deg F (205 deg C), a maximum working pressure of 250 psig (1724 kPa), and for glycol solutions.

          - Seal: Mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Viton bellows and gasket.

          - Seal: Packing seal consisting of stuffing box with a minimum of four rings of graphite-impregnated braided yarn with bronze lantern ring between center two graphite rings, and bronze packing gland.

          - Pump Bearings: Grease-lubricated ball bearings in cast-iron housing with grease fittings.

Not all manufacturers provide a back-pullout coupling design that allows removal and replacement of impeller without disconnecting piping. The Flo fab coupling is located inside the "power frame", permitting the servicing of the pump, mechanical seal, wear ring, bearings, and impeller without disturbing the piping connections.  Coupling alignment is NOT required.  The pump and motor are self-aligning.

        - Shaft Coupling and Guard, Motors Larger than 5-hp (3.73 kW): Flexible coupling with steel hubs and rubber sleeve between the pump and motor shaft, inside steel power frame coupling guard.

        - Motor: Single speed, secured to mounting frame, with adjustable alignment.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

            - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient<, inverter-duty> <Insert designation>.

            - NEMA Design: B <Insert designation>.

            - Service Factor: 1.15 <Insert value>.

If Project has more than one type or configuration of separately coupled, base-mounted, end-suction centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

Select motors to allow the pump to operate at maximum capacity without surpassing the amperage draw.

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1720 kPa)] [300 psig (2068 kPa)].

          - Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)] [400 deg F (205 deg C)].

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

Flo Fab also offers motors with voltages of 3,300-, 6,600-, 11,000-, and 13,600-V ac.  Contact the factory.

            - Volts: [120] [240] [208] [380] [460] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: [60] [50].

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - SEPARATELY COUPLED, HORIZONTALLY MOUNTED, IN-LINE CENTRIFUGAL PUMPS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; XRI Series or comparable product by one of the following:

          - Flowserve Corporation.

          - ITT Corporation.

          - KUBOTA Corporation.

          - Mepco, LLC.

          - Naniwa Pump Mfg Co., Ltd.

          - PACO Pumps; Grundfos Pumps Corporation, USA.

          - Scot Pump; a division of Ardox Corporation.

          - Thrush Co. Inc.

        - Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, in-line pump as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted horizontally.

        - Pump Construction:

The Flo Fab pump is a back-pullout design, fully serviceable at site by removing the impeller housing which includes impeller, bearings, and mechanical seal in vertical or horizontal positions, without disturbing the piping connections or removing the motor.  All bearings an integral part of the impeller housing.

For easy service on site and to avoid vibrations and high failure rates pumps with shafts supported by the motor bearings are not allowed, to ensure total cost of ownership and quick economical operational life all pumps to be supplied with standard generic motors, seals and bearings, pumps with proprietary or exclusive motors, seals or bearings are not allowed.

For durability pump should be supplied with both casing and impeller wearing rings.

          - Casing: Radially split, cast iron, with threaded gage tappings at inlet and outlet, and threaded [companion-flange] [union-end] connections.

          - Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, and keyed to shaft. For pumps not frequency-drive controlled, trim impeller to match specified performance.

          - Pump Shaft:  Stainless steel.

In "Mechanical Seal" Subparagraph below, retain "Buna-N" option for temperature rating of 225 deg F (107 deg C); retain "EPT" option for 250 deg F (120 deg C).

          - Mechanical Seal: Carbon rotating ring against a ceramic seat held by a stainless-steel spring, and [Viton] [Buna-N] [EPT] bellows and gasket. Include water slinger on shaft between motor and seal.

          - Pump Bearings: [Permanently lubricated ball bearings] [Oil lubricated; bronze-journal or thrust type].

Not all manufacturers provide a back-pullout coupling design that allows removal and replacement of impeller without disconnecting piping. The Flo fab coupling is located inside the "power frame", permitting the servicing of the pump, mechanical seal, wear ring, bearings, and impeller without disturbing the piping connections.  Coupling alignment is NOT required.  The pump and motor are self-aligning.

        - Shaft Coupling: [Molded-rubber insert with interlocking spider] [Interlocking frame with interconnecting springs] capable of absorbing vibration.

        - Motor: Single speed and [resiliently] [rigidly] mounted to pump casing.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

            - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient<, inverter-duty> <Insert designation>.

            - NEMA Design: <Insert designation>.

            - Service Factor: <Insert value>.

If Project has more than one type or configuration of separately coupled, horizontally mounted, in-line centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: 175 psig (1204 kPa).

          - Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)].

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

Flo Fab also offers motors with voltages of 3,300-, 6,600-, 11,000-, and 13,600-V ac.  Contact the factory.

            - Volts: [120] [240] [208] [460] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - SEPARATELY COUPLED, VERTICALLY MOUNTED, IN-LINE CENTRIFUGAL PUMPS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; [840SC] [880RI] or comparable product by one of the following:

          - ITT Corporation.

          - KUBOTA Corporation.

          - Mepco, LLC.

          - Naniwa Pump Mfg Co., Ltd.

          - PACO Pumps; Grundfos Pumps Corporation, USA.

          - Patterson Pump Company; a Gorman-Rupp company.

          - Peerless Pump Company.

          - Thrush Co. Inc.

        - Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, in-line pump as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted vertically.

        - Pump Construction:

Not all manufacturers provide volute supports that allow removal and replacement of impeller without disconnecting piping.

The Flo Fab pump is a back-pullout design, fully serviceable at site by removing the impeller housing which includes impeller, bearings, and mechanical seal in vertical or horizontal positions, without disturbing the piping connections or removing the motor.  All bearings an integral part of the impeller housing.

For easy service on site and to avoid vibrations and high failure rates pumps with shafts supported by the motor bearings are not allowed, to ensure total cost of ownership and quick economical operational life all pumps to be supplied with standard generic motors, seals and bearings, pumps with proprietary or exclusive motors, seals or bearings are not allowed.

For durability pump should be supplied with both casing and impeller wearing rings.

          - Casing: ASTM A48, Class 30, radially split, cast iron, with threaded gage tappings at inlet and outlet[, replaceable bronze wear rings,] and suction and discharge flanged connections [Class 125][Class 250], and solid base with four anchor holes.

          - Impeller: ASTM B 584, cast bronze, closed type; statically and dynamically balanced, keyed to shaft, and secured with a stainless steel bolt and washer. For pumps not frequency-drive controlled, trim impeller to match specified performance.

          - Pump Shaft:  Stainless steel, fitted with bronze sleeve and Buna-N O-ring.

Mechanical seal is suitable for service temperatures above 200 deg F (93 deg C). The "Viton" bellow is for a maximum working temperature of 400 deg F (205 deg C), a maximum working pressure of 250 psig (1724 kPa), and for glycol solutions.

          - Seal: Self-lubricating mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Viton bellows and gasket.

          - Pump Bearings: [Permanently lubricated ball bearings] [Oil lubricated; bronze-journal or thrust type].

Not all manufacturers provide drop-out coupling that allows removal and replacement of impeller without disconnecting piping. The Flo fab coupling is located inside the "power frame", permitting the servicing of the pump, mechanical seal, wear ring, impeller without disturbing the piping connections.  Coupling alignment is NOT required.  The pump and motor are self-aligning.

        - Shaft Coupling and Guard, Motors Larger than 5-hp (3.73 kW): Rigid, self-aligning, steel coupling between the pump and motor shaft, inside steel power frame coupling guard.

        - Motor: Single speed and rigidly mounted to pump casing with lifting eyebolt and supporting lugs in motor enclosure, TC motor type.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

            - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient<, inverter-duty> <Insert designation>.

            - NEMA Design: B <Insert designation>.

            - Service Factor: 1.15 <Insert value>.

        - Accessories:

          - Flow Meter: Pitot tube flow meter for field installation on the casing discharge, model [FMI] <Insert designation>.

          - Casing Drain Valve: Drain valve with bronze cap for field installation on the casing discharge, model [HN0050] <Insert designation>.

If Project has more than one type or configuration of separately coupled, vertically mounted, in-line centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

Select motors to allow the pump to operate at maximum capacity without surpassing the amperage draw.

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1720 kPa)].

          - Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)] [400 deg F (205 deg C)].

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

Flo Fab also offers motors with voltages of 3,300-, 11,000-, and 13,600-V ac.  Contact the factory.

            - Volts: [120] [240] [208] [380] [460] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: [60] [50].

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - SEPARATELY COUPLED, BASE-MOUNTED, END-SUCTION CENTRIFUGAL PUMPS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; [2000] [2600] pump or comparable product by one of the following:

          - ITT Corporation.

          - KUBOTA Corporation.

          - Mepco, LLC.

          - Naniwa Pump Mfg Co., Ltd.

          - PACO Pumps; Grundfos Pumps Corporation, USA.

          - Peerless Pump Company.

          - Scot Pump; a division of Ardox Corporation.

          - Thrush Co. Inc.

        - Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, end-suction pump as defined in HI 1.1-1.2 and HI 1.3; designed for base mounting, with pump and motor shafts horizontal.

        - Pump Construction:

The Flo Fab pump is a back-pullout design, fully serviceable at site by removing the impeller housing which includes impeller, bearings, and mechanical seal in vertical or horizontal positions, without disturbing the piping connections or removing the motor.  All bearings an integral part of the impeller housing.

For easy service on site and to avoid vibrations and high failure rates pumps with shafts supported by the motor bearings are not allowed, to ensure total cost of ownership and quick economical operational life all pumps to be supplied with standard generic motors, seals and bearings, pumps with proprietary or exclusive motors, seals or bearings are not allowed.

For durability pump should be supplied with both casing and impeller wearing rings.

          - Casing: ASTM A48, Class 30, radially split, cast iron, with[ replaceable bronze wear rings,] threaded gage tappings at inlet and outlet, drain plug at bottom and air vent at top of volute, and [threaded companion-flange] [flanged] connections.[ Provide integral mount on volute to support the casing, and provide attached piping to allow removal and replacement of impeller without disconnecting piping or requiring the realignment of pump and motor shaft.]

          - Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, keyed to shaft, and secured with a stainless steel bolt and washer. For pumps not frequency-drive controlled, trim impeller to match specified performance.

          - Pump Shaft: [Steel, with copper-alloy shaft sleeve] [Stainless steel].

Mechanical seal is suitable for service temperatures above 200 deg F (93 deg C). The "Viton" bellow is for a maximum working temperature of 400 deg F (205 deg C), a maximum working pressure of 250 psig (1724 kPa), and for glycol solutions.

          - Seal: Mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Viton bellows and gasket.

          - Pump Bearings: Grease-lubricated ball bearings in cast-iron housing with grease fittings.

Not all manufacturers provide drop-out coupling that allows removal and replacement of impeller without disconnecting piping. This device is required with volute support described in "Casing" Subparagraph above.

        - Shaft Coupling: Molded-rubber insert and interlocking spider capable of absorbing vibration. [Couplings shall be drop-out type to allow disassembly and removal without removing pump shaft or motor.] [EPDM coupling sleeve for variable-speed applications.]

        - Coupling Guard: Dual rated; ANSI B15.1, Section 8; OSHA 1910.219 approved; steel; removable; attached to mounting frame.

        - Mounting Frame: Welded-steel frame and cross members, factory fabricated from ASTM A 36/A 36M channels and angles. Fabricate to mount pump casing, coupling guard, and motor.

        - Motor: Single speed, secured to mounting frame, with adjustable alignment.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

            - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient<, inverter-duty> <Insert designation>.

            - NEMA Design: <Insert designation>.

            - Service Factor: <Insert value>.

If Project has more than one type or configuration of separately coupled, base-mounted, end-suction centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1720 kPa)] [300 psig (2068 kPa)].

          - Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)] [400 deg F (205 deg C)].

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

Flo Fab also offers motors with voltages of 3,300-, 11,000-, and 13,600-V ac.  Contact the factory.

            - Volts: [120] [240] [208] [380] [460] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: [60] [50].

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - SEPARATELY COUPLED, BASE-MOUNTED, DOUBLE-SUCTION CENTRIFUGAL PUMPS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; [4800] [4800H] [4800L] [4800U] or comparable product by one of the following:

          - Crane Pumps & Systems.

          - Flowserve Corporation.

          - ITT Corporation.

          - Scot Pump; a division of Ardox Corporation.

          - Thrush Co. Inc.

        - Description: Factory-assembled and -tested, centrifugal, impeller-between-bearings, separately coupled, double-suction pump as defined in HI 1.1-1.2 and HI 1.3; designed for base mounting, with pump and motor shafts horizontal.

        - Pump Construction:

The Flo Fab pump is a back-pullout design, fully serviceable at site by removing the impeller housing which includes impeller, bearings, and mechanical seal in vertical or horizontal positions, without disturbing the piping connections or removing the motor.  All bearings an integral part of the impeller housing.

For easy service on site and to avoid vibrations and high failure rates pumps with shafts supported by the motor bearings are not allowed, to ensure total cost of ownership and quick economical operational life all pumps to be supplied with standard generic motors, seals and bearings, pumps with proprietary or exclusive motors, seals or bearings are not allowed.

For durability pump should be supplied with both casing and impeller wearing rings.

          - Casing: [Radially] [Horizontally] split, cast iron, with[ replaceable bronze wear rings,] threaded gage tappings at inlet and outlet, drain plug at bottom and air vent at top of volute, and ASME B16.1, [Class 125] [Class 250] flanges.[ Casing supports shall allow removal and replacement of impeller without disconnecting piping.]

          - Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, and keyed to shaft. For pumps not frequency-drive controlled, trim impeller to match specified performance.

          - Pump Shaft: Stainless steel with two support points and shoulders machined into the shaft ready to receive the ball bearing.

Mechanical seal is suitable for service temperatures above 200 deg F (93 deg C). The "Viton" bellow is for a maximum working temperature of 400 deg F (205 deg C), a maximum working pressure of 250 psig (1724 kPa), and for glycol solutions.

          - Seal: Mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Viton bellows and gasket.

          - Pump Bearings: Grease-lubricated ball bearings in cast-iron housing with grease fittings.

Not all manufacturers provide drop-out coupling that allows removal and replacement of impeller without disconnecting piping. This device is required with casing support described in "Casing" Subparagraph above.

The Flo Fab coupling is designed for easy disassembly, allowing removal of the bearing housing and impeller without disturbing the alignment between the volute and motor.  The coupling will absorb extreme torsional shock and vibration.  A removable guard attached to the base provides protection to maintenance personnel.

        - Shaft Coupling: Molded-rubber insert and interlocking spider capable of absorbing vibration. [Couplings shall be drop-out type to allow disassembly and removal without removing pump shaft or motor.] [EPDM coupling sleeve for variable-speed applications.]

        - Coupling Guard: Dual rated; ANSI B15.1, Section 8; OSHA 1910.219 approved; steel; removable; attached to mounting frame.

        - Mounting Frame: Welded-steel frame and cross members, factory fabricated from ASTM A 36/A 36M channels and angles. Fabricate to mount pump casing, coupling guard, and motor.

        - Motor: Single speed, secured to mounting frame, closed type, foot mounted, with adjustable alignment.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

            - Motor Bearings: Grease lubricated.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient<, inverter-duty> <Insert designation>.

            - NEMA Design: <Insert designation>.

            - Service Factor: <Insert value>.

If Project has more than one type or configuration of separately coupled, base-mounted, double-suction centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1720 kPa)] [300 psig (2068 kPa)].

          - Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)] [400 deg F (205 deg C)].

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

Flo Fab also offers motors with voltages of 3,300-, 6,600-, 11,000-, and 13,600-V ac.  Contact the factory.

            - Volts: [120] [240] [208] [380] [460] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: [60] [50].

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - SEPARATELY COUPLED, VERTICALLY MOUNTED, DOUBLE-SUCTION CENTRIFUGAL PUMPS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; 4800V or comparable product by one of the following:

          - Crane Pumps & Systems.

          - Flowserve Corporation.

          - ITT Corporation.

          - Scot Pump; a division of Ardox Corporation.

          - Thrush Co. Inc.

        - Description: Factory-assembled and -tested, centrifugal, impeller-between-bearings, separately coupled, double-suction pump as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted vertically.

        - Pump Construction:

The Flo Fab pump is a back-pullout design, fully serviceable at site by removing the impeller housing which includes impeller, bearings, and mechanical seal in vertical or horizontal positions, without disturbing the piping connections or removing the motor.  All bearings an integral part of the impeller housing.

For easy service on site and to avoid vibrations and high failure rates pumps with shafts supported by the motor bearings are not allowed, to ensure total cost of ownership and quick economical operational life all pumps to be supplied with standard generic motors, seals and bearings, pumps with proprietary or exclusive motors, seals or bearings are not allowed.

For durability pump should be supplied with both casing and impeller wearing rings.

          - Casing: Radially split, cast iron, with[ replaceable bronze wear rings,] threaded gage tappings at inlet and outlet, drain plug at bottom of volute, mounting support, and ASME B16.1, [Class 125] [Class 250] flanges.

          - Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, and keyed to shaft. For pumps not frequency-drive controlled, trim impeller to match specified performance.

          - Pump Shaft: Stainless steel with two support points and shoulders machined into the shaft ready to receive the ball bearing.

Mechanical seal is suitable for service temperatures above 200 deg F (93 deg C). The "Viton" bellow is for a maximum working temperature of 400 deg F (205 deg C), a maximum working pressure of 250 psig (1724 kPa), and for glycol solutions.

          - Seal: Mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and Viton bellows and gasket.

          - Pump Bearings: Grease-lubricated ball bearings in cast-iron housing with grease fittings.

The Flo Fab coupling is designed for easy disassembly, allowing removal of the bearing housing and impeller without disturbing the alignment between the volute and motor.  The coupling will absorb extreme torsional shock and vibration.  A removable guard attached to the base provides protection to maintenance personnel.

        - Shaft Coupling: Molded-rubber insert and interlocking spider capable of absorbing vibration.

        - Motor: Single speed, closed type, foot mounted, and secured to casing.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

            - Motor Bearings: Grease lubricated.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient<, inverter-duty> <Insert designation>.

            - NEMA Design: <Insert designation>.

            - Service Factor: <Insert value>.

If Project has more than one type or configuration of separately coupled, vertically mounted, double-suction centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1720 kPa)] [300 psig (2068 kPa)].

          - Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)] [400 deg F (205 deg C)].

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

Flo Fab also offers motors with voltages of 3,300-, 6,600-, 11,000-, and 13,600-V ac.  Contact the factory.

            - Volts: [120] [240] [208] [380] [460] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: [60] [50].

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - SEPARATELY COUPLED, VERTICALLY MOUNTED, TURBINE CENTRIFUGAL PUMPS

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

          - American-Marsh Pumps.

          - Aurora Pump; Pentair Ltd.

          - Crane Pumps & Systems.

          - Flowserve Corporation.

          - Mepco, LLC.

          - PACO Pumps; Grundfos Pumps Corporation, USA.

          - Patterson Pump Company; a Gorman-Rupp company.

          - Peerless Pump Company.

          - Pentair Water.

          - <Insert manufacturer's name>.

        - Description: Factory-assembled and -tested, [single-stage] [multistage], centrifugal, impeller-between-bearings, end-suction pump as defined in HI 2.1-2.2 and HI 2.3; designed for installation with pump and motor shafts mounted vertically and projecting into a sump.

        - Pump Construction:

          - Pump Bowl: Cast iron, with [cone] [basket] strainer[, replaceable bronze wear ring,] and suction bell.[ Water passages of intermediate bowls shall be coated with porcelain enamel.]

          - Impeller: ASTM B 584, cast bronze; statically and dynamically balanced and keyed to shaft. For pumps not frequency-drive controlled, trim impeller to match specified performance.

          - Pump Shaft: [Carbon] [Stainless] steel sized according to manufacturer's requirements.

          - Pump Bearings: Water-lubricated bronze and rubber sleeve bearings in cast-iron housing.

          - Pump Column: ASTM A 53/A 53M, Grade B steel pipe.

Retain one of two "Seal" subparagraphs below. Retain first subparagraph for service temperatures above 200 deg F (93 deg C); retain second subparagraph for service temperatures 200 deg F (93 deg C) or lower. In first subparagraph below, retain "Buna-N" option for temperature rating of 225 deg F (107 deg C); retain "EPT" option for 250 deg F (120 deg C) and for glycol solutions.

          - Seal: Mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and [Buna-N] [EPT] bellows and gasket. Include water slinger on shaft between motor and seal.

          - Seal: Packing seal consisting of stuffing box with a minimum of four rings of graphite-impregnated braided yarn with bronze lantern ring between center two graphite rings, and bronze packing gland.

        - Shaft Coupling: Keyed with locking collets.

        - Discharge Head: ASME B16.1, [Class 125] [Class 250] discharge flange with threaded gage tapping. Top of discharge head shall have a registered fit to accurately locate the driver.

        - Drive Ratchet: Nonreversing ratchet.

        - Hollow Shaft Motor: Single speed and secured to discharge head.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

            - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

            - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

            - Motor Bearings: Grease lubricated.

            - Unusual Service Conditions:

              - Ambient Temperature: <Insert deg C>.

              - Altitude: <Insert feet (meters)> above sea level.

              - High humidity.

              - <Insert conditions>.

            - Efficiency: Premium efficient.

            - NEMA Design: <Insert designation>.

            - Service Factor: <Insert value>.

If Project has more than one type or configuration of separately coupled, vertically mounted, turbine centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Minimum Static Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: 175 psig (1204 kPa).

          - Maximum Continuous Operating Temperature: 200 deg F (93 deg C).

          - Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: [120] [240] [208] [460] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - SINGLE/TWIN WET-ROTOR PUMPS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; 500 Series or comparable product by one of the following:

          - ITT Corporation.

          - KUBOTA Corporation.

          - Mepco, LLC.

          - Naniwa Pump Mfg Co., Ltd.

          - PACO Pumps; Grundfos Pumps Corporation, USA.

          - Peerless Pump Company.

          - Scot Pump; a division of Ardox Corporation.

          - Thrush Co. Inc.

        - Description: Factory-assembled and -tested, wet-rotor pump.

        - Pump Construction:

          - Body: Cast iron.

          - Impeller: Technopolymer.

          - Pump Shaft: Hardened stainless steel .

          - Bearings: Ceramic bearings lubricated by the pumping medium.

          - Enbloc Circulator: Cast iron hydraulic section and wet rotor synchronous motor.

          - Motor Casing: Aluminum.

          - Pump Body:  Scroll type with high hydraulic efficiency and smooth internal surfaces.

          - Ports: Flanged suction and discharge ports equipped with threaded fittings for pressure and temperature readings.

          - Single Pump: Standard with insulating covers.

          - Twin Pump: Insulation of the twin version is to be provided by the installer.

Use special caution to avoid obstructing the condensate drainage labyrinths in order to avoid impairing operation.

          - Rotor Protective Jacket: Stainless steel.

          - Thrust Ring: Ceramic with ethylene or propylene seals and stator jacket in carbon fiber composite.

          - Swing Check Valve: Twin version is equipped with an automatic swing check valve incorporated in the discharge port to avoid water recirculating through the unit when it is not running; a blank flange to be supplied as standard to allow either of the two motors to be removed for servicing.

          - Pump Body: Standard is PN 16. Both the NPS 3 (DN 80) and the NPS 4 (DN 100) PN 16 (8 holes) versions are options.

        - Motor: [Single] [Variable] speed, permanent magnet synchronous motor.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

            - Efficiency: Premium efficient.

            - NEMA Design: <Insert designation>.

            - Service Factor: <Insert value>.

        - Wet rotors are controlled by an IGBT-based device in NPT-technology.  Specific features include:

          - Sine wave modulated PWM.

          - High carrier frequency to eliminate all audio band noise.

          - Two dedicated 32-bit processors. One is dedicated to the motor control and one is dedicated to the user interface allowing the following functions:

            - Start/stop control.

            - Economy control.

            - 0 -10 V dc analog signal control.

            - PWM signal control.

            - 4-20 mA analog signal control.

            - Temperature sensor signal control.

            - Connection to ModBus control systems.

            - Optional LonWorks with relative module.

            - Optimized space vector algorithm.

            - Alarm system availability.

            - Indication pump running.

If Project has more than one type or configuration of wet-rotor pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Operating Pressure: 150 psig (1132 kPa).

          - Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [230 deg F (111 deg C)].

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Impeller Size: <Insert inches (mm)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: [120] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - MODULAR PACKAGED PUMP SYSTEMS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model [D-HC-VFD] or comparable product by the following:

          - <Insert manufacturer's name>.

        - Description: Factory-assembled and -tested, fluid-handling system for hydronic systems, with pumps, piping, valves, specialties, and controls, and mounted on base.

The Flo Fab Model HC pump package consists of two (enter number) pumps, control panel with variable frequency controller (VFC), expansion tank, air separator, chemical bypass feeder, heat exchangers (shell and tube/plate), boilers, chillers, cooling towers, glycol fill system (optional), balancing valves, isolation valves, air vents, drains, multifunction valves, suction diffusers (or Y-pattern strainers), and interconnecting black steel schedule 40 piping.  All package components are mounted on a structural steel base with lifting lugs.  Assembly, testing, and final adjusting is performed at the factory.  The module will be onsite ready for mechanical and electrical system connections.

Edit centrifugal pump articles above and edit the "Pumps" paragraph below; first paragraph describes the vertically mounted, double suction pump used with the Model HC package.

        - Pumps:

          - Type: [Separately coupled, vertically mounted, double-suction pump, Flo Fab Select Series] <Insert pump designation> as defined in centrifugal pump Articles above.

          - Mounting: [Vertical/Horizontal floor mounted] <Insert mounting>.

          - Number of Pumps: [Two] <Insert Number>.

        - Dual-temperature heating and cooling water piping, [NPS 2 (DN 50) and smaller] <Insert pipe size range>, shall be the following:

          - [Schedule 40] [Schedule 30] [Schedule 20] steel pipe; [Class 125, cast-iron] [Class 150, malleable-iron] [Class 250, cast-iron] [Class 300, malleable-iron] fittings; cast-iron flanges and flange fittings; and threaded joints.

        - Dual-temperature heating and cooling water piping, [NPS 2-1/2 (DN 65) and larger] <Insert pipe size range>, shall be the following:

          - [Schedule 40] [Schedule 30] [Schedule 20] steel pipe, wrought-steel fittings and wrought-cast or forged-steel flanges and flange fittings, and welded and flanged joints.

        - Makeup-water piping, NPS 3/4 (DN 20), shall have a shut-off valve and manual bypass with the following:

          - [Type L (Type B)] [Type M (Type C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.

          - Diaphragm-Operated, Pressure-Reducing Valve: ASME labeled.

          - Inlet Strainer: <Insert materials>, removable without system shutdown.

          - Direct-Mounted, Metal-Case, Dial-Type Pressure Gage.

        - Replaceable Bladder-Type Expansion Tanks:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Series BT or comparable product by the following:

            - <Insert manufacturer's name>.

          - Tank: Welded steel, rated for 125-psig (860-kPa) working pressure and 375 deg F (191 deg C) maximum operating temperature. Factory test after taps are fabricated and supports installed and are labeled according to ASME Boiler and Pressure Vessel Code: Section VIII, Division 1.

          - Bladder: Securely sealed into tank to separate air charge from system water to maintain required expansion capacity.

              - Butyl Rubber, compatible with water or ethylene glycol.

              - EPDM, compatible with propylene glycol.

          - Air-Charge Fittings: Schrader valve, stainless steel with EPDM seats.

For heating and cooling systems the pre-charge is equal to the system fill pressure.

            - Description:

              - Capacity: <Insert gal (L)>.

              - Diameter: <Insert inches (mm)>.

              - Height: <Insert inches (mm)>.

            - Orientation: [Horizontal saddles] [Vertical base] <Insert orientation>.

        - Tangential-Type Air Separators:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model SEP or comparable product by the following:

            - <Insert manufacturer's name>.

          - Tank: Welded steel; ASME constructed and labeled for [125-psig (860-kPa)] [150-psig (1034-kPa)] minimum working pressure and 450 deg F (232 deg C) maximum operating temperature.

Delete the strainer subparagraph below for air separators without strainers.

          - Strainer: [Galvanized steel screen] [Stainless steel 304 screen] [Stainless steel 316 screen].

          - Tangential Inlet and Outlet Connections: Threaded for NPS 2 (DN 50) and smaller; flanged connections for NPS 2-1/2 (DN 65) and larger.

          - Vent Connection: Threaded.

          - Blowdown Connection: Threaded.

          - Size: Match system flow capacity.

        - Combination Air and Sediment Separators:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model ADSR or comparable product by the following:

            - <Insert manufacturer's name>.

          - Tank: Welded steel; ASME constructed and labeled for 125-psig (860-kPa) minimum working pressure and 250 deg F (121 deg C) maximum operating temperature.

          - Coalescing Medium: Stainless steel.

          - End Inlet and Outlet Connections: Threaded for NPS 2 (DN 50) and smaller; flanged connections for NPS 2-1/2 (DN 65) and larger.

          - Vent Connection: Threaded.

          - Blowdown Connection: Threaded.

          - Skim Valve Connection: Threaded.

          - Head: Removable.

          - Size: Match system flow capacity.

        - Chemical Bypass Feeder: Steel, with corrosion-resistant exterior coating, minimum 3-1/2-inch (89-mm) fill opening in the top, and NPS 3/4 (DN 20) bottom inlet and top side outlet. Quarter turn or threaded fill cap with gasket seal and diaphragm to lock the top on the feeder when exposed to system pressure in the vessel.

          - Capacity: [2 gal. (7.6 L)] [5 gal. (19 L)] <Insert value>.

          - Minimum Working Pressure: [125 psig (860 kPa)] [175 psig (1210 kPa)] [300 psig (2068 kPa)] <Insert value>.

        - Cooling Towers: Refer to Division 23 Sections for cooling towers.

        - Boilers: Refer to Division 23 Sections for boilers.

        - Chillers: Refer to Division 23 Sections for chillers.

        - Shut Off Valves:

          - Bronze Ball Valves, Two-Piece with Full Port and Stainless-Steel Trim:

            - Standard: MSS SP-110.

            - SWP Rating: 150 psig (1035 kPa).

            - CWP Rating: 600 psig (4140 kPa).

            - Body Design: Two piece.

            - Body Material: Bronze.

            - Ends: Threaded.

            - Seats: PTFE.

            - Stem: Stainless steel.

            - Ball: Stainless steel, vented.

            - Port: Full.

          - Iron, Single-Flange Butterfly Valves with Stainless-Steel Disc:

            - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Series LBFVZ or comparable product by the following:

              - <Insert manufacturer's name>.

            - Standard: MSS SP-67, Type I.

            - CWP Rating: [150 psig (1035 kPa)] [200 psig (1380 kPa)].

            - Body Design: Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

            - Body Material: ASTM A 126, cast iron or ASTM A 536, ductile iron.

            - Seat: [EPDM] [NBR].

            - Stem: One- or two-piece stainless steel.

            - Disc: Stainless steel.

          - Bronze Lift Check Valves with Bronze Disc, Class 125:

            - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Series STB or comparable product by the following:

              - <Insert manufacturer's name>.

            - Standard: MSS SP-80, Type 1.

            - CWP Rating: 200 psig (1380 kPa).

            - Body Design: Vertical flow.

            - Body Material: ASTM B 61 or ASTM B 62, bronze.

            - Ends: Threaded.

            - Disc: Bronze.

          - Iron, Compact-Wafer, Center-Guided Check Valves with Resilient Seat, Class 125:

            - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Series LSDDB or comparable product by the following:

              - <Insert manufacturer's name>.

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Material: ASTM A 126, gray iron.

            - Style: Compact wafer.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

          - Shutoff Valves NPS 2 (DN 50) and Smaller:  Two-piece, full-port ball valve.

          - Shutoff Valves NPS 2-1/2 (DN 65) and Larger:  Lug-type butterfly valve, in each pump's suction and discharge piping[ and in inlet and outlet headers].

          - Check Valves NPS 2 (DN 50) and Smaller: [Lift] [or] [swing] type in each pump's discharge piping.

          - Check Valves NPS 2-1/2 (DN 65) and Larger: Wafer type in each pump's discharge piping.

        - Bronze, Calibrated-Orifice, Balancing Valves:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model LGS or comparable product by the following:

            - <Insert manufacturer's name>.

          - Body: Bronze, ball or plug type with calibrated orifice or venturi.

          - Ball: Brass or stainless steel.

          - Plug: Resin.

          - Seat: PTFE.

          - End Connections: Threaded or socket.

          - Pressure Gage Connections: Integral seals for portable differential pressure meter.

          - Handle Style: Lever, with memory stop to retain set position.

          - CWP Rating: Minimum 125 psig (860 kPa).

          - Maximum Operating Temperature: 250 deg F (121 deg C).

        - Cast-Iron or Steel, Calibrated-Orifice, Balancing Valves:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model LGS or comparable product by the following:

            - <Insert manufacturer's name>.

          - Body: Cast-iron or steel body, ball, plug, or globe pattern with calibrated orifice or venturi.

          - Ball: Brass or stainless steel.

          - Stem Seals: EPDM O-rings.

          - Disc: Glass and carbon-filled PTFE.

          - Seat: PTFE.

          - End Connections: Flanged or grooved.

          - Pressure Gage Connections: Integral seals for portable differential pressure meter.

          - Handle Style: Lever, with memory stop to retain set position.

          - CWP Rating: Minimum 125 psig (860 kPa).

          - Maximum Operating Temperature: 250 deg F (121 deg C).

        - Y-Pattern Strainers:

          - Body: ASTM A 126, Class B, cast iron with bolted cover and bottom drain connection.

          - End Connections: Threaded ends for NPS 2 (DN 50) and smaller; flanged ends for NPS 2-1/2 (DN 65) and larger.

In "Strainer Screen" Subparagraph below, larger mesh numbers have larger passages, thus allowing larger objects to pass.

          - Strainer Screen: Stainless-steel, [20] [40] [60]-mesh strainer, or perforated stainless-steel basket.

          - CWP Rating: 125 psig (860 kPa).

        - Suction Diffusers:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model ASDFF or comparable product by the following:

            - <Insert manufacturer's name>.

          - Angle pattern.

          - [175-psig (1204-kPa)] [300-psig (2060-kPa)] pressure rating, [cast] [ductile]-iron body and end cap, pump-inlet fitting.

          - Bronze startup and bronze or stainless-steel permanent strainers.

          - Bronze or stainless-steel straightening vanes.

          - Drain plug.

          - Factory-fabricated support.

        - Multi-Function Valves:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model MFV or comparable product by the following:

            - <Insert manufacturer's name>.

          - Angle or straight pattern.

          - [175-psig (1204-kPa)] [300-psig (2060-kPa)] pressure rating, [cast] [ductile]-iron body, pump-discharge fitting.

          - Drain plug and bronze-fitted shutoff, balancing, and check valve features.

          - Brass gage ports with integral check valve and orifice for flow measurement.

        - Metal-Case, Industrial-Style, Liquid-in-Glass Thermometers:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model L9VU or comparable product by the following:

            - <Insert manufacturer's name>.

          - Standard: ASME B40.200.

          - Case: [Cast aluminum] <Insert material>; [7-inch (178-mm)] [9-inch (229-mm)] nominal size unless otherwise indicated.

          - Case Form: [Adjustable angle] [Back angle] [Straight] <Insert form> unless otherwise indicated.

          - Tube: Glass with magnifying lens and blue[ or red] organic liquid.

          - Tube Background: Nonreflective aluminum with permanently etched scale markings graduated in [deg F (deg C)] [deg F and deg C].

          - Window: [Glass] [or] [plastic] <Insert material>.

          - Stem: [Aluminum] <Insert material> and of length to suit installation.

            - Design for Thermowell Installation: Bare stem.

          - Connector: 1-1/4 inches (32 mm), with ASME B1.1 screw threads.

          - Accuracy: Plus or minus 1 percent of scale range or one scale division, to a maximum of 1.5 percent of scale range.

          - Scale Range for Chilled-Water Piping: [0 to 120 deg F (Minus 20 to plus 49 deg C)].

          - Scale Range for Heating, Hot-Water Piping: [32 to 240 deg F (0 to 150 deg C)].

          - Scale Range for Low Temperature Hot-Water Piping: [32 to 180 deg F (0 to 115 deg C)].

          - Scale Range for Domestic Water Piping: [32 to 180 deg F (0 to 115 deg C)].

        - Direct-Mounted, Metal-Case, Dial-Type Pressure Gage.

          - Pumps, control panel and all other accessories will be piped, fitted and electrically wired together and then shall go through mechanical, electrical and hydrostatic verification before shipment.

          - A solid foundation will be provided to absorb any vibration and provide a firm support system. The bolts will be embedded in the concrete with sockets to allow the adjustment of bolts after the concrete has been poured. The system will be placed on this foundation, carefully levelled and bolted down.

          - Standard: ASME B40.100.

          - Case: [Liquid-filled] [Sealed] [Open-front, pressure relief] [Solid-front, pressure relief] <Insert type> type(s); [cast aluminum or drawn steel] <Insert material>; [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert dimension> nominal diameter.

          - Pressure-Element Assembly: Bourdon tube unless otherwise indicated.

Match pressure connection size in first subparagraph below with gage attachment size.

          - Pressure Connection: Brass, with [NPS 1/4 (DN 8)] [NPS 1/4 or NPS 1/2 (DN 8 or DN 15)] [NPS 1/2 (DN 15)], ASME B1.20.1 pipe threads and bottom-outlet type unless back-outlet type is indicated.

          - Movement: Mechanical, with link to pressure element and connection to pointer.

          - Dial: Nonreflective aluminum with permanently etched scale markings graduated in [psi (kPa)] [psi and kPa].

          - Pointer: Dark-colored metal.

          - Window: [Glass] [or] [plastic] <Insert material>.

          - Ring: [Metal] [Brass] [Stainless steel].

          - Accuracy: [Grade A, plus or minus 1 percent of middle half of] [Grade B, plus or minus 2 percent of middle half of] [Grade C, plus or minus 3 percent of middle half of] [Grade D, plus or minus 5 percent of whole] scale range.

        - Dielectric Fittings: With insulating material isolating joined dissimilar metals.

        - Stainless-Steel Bellow, Flexible Connectors:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model [ST] [SM] or comparable product by the following:

            - <Insert manufacturer's name>.

          - Body: Stainless-steel bellows with woven, flexible, bronze, wire-reinforcing protective jacket.

          - End Connections: Threaded or flanged to match equipment connected.

          - Performance: Capable of 3/4-inch (20-mm) misalignment.

          - CWP Rating: 150 psig (1035 kPa).

          - Maximum Operating Temperature: 250 deg F (121 deg C).

        - Spherical, Rubber, Flexible Connectors:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model [DUT] [or] [DSP], or comparable product by the following:

            - <Insert manufacturer's name>.

          - Body: Fiber-reinforced rubber body.

          - End Connections: Steel flanges drilled to align with Classes 150 and 300 steel flanges.

          - Performance: Capable of misalignment.

Retain "Control Rods" and "Control Plates" to protect flexible connector from excessive deformation.

          - Control Rods: Painted carbon steel.

          - Control Plates: Nickel iron.

          - CWP Rating: 150 psig (1035 kPa).

          - Maximum Operating Temperature: 250 deg F (121 deg C).

        - Control Panel: Factory installed and connected as an integral part of pump package; automatic for multiple-pump, variable-speed operation, with load control and protection functions.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Model DP Duplex Control Panel, or comparable product by the following:

            - <Insert manufacturer's name>.

          - Control Logic: Solid-state system with transducers, programmable microprocessor, VFC, and other devices in controller. Install VFC for pump motors larger than 25 hp in separate panel; same type as motor control panel enclosure.

          - Motor Controller: NEMA ICS 2, variable-frequency, solid-state type.

Revise "Control Voltage" Subparagraph below if required.

            - Control Voltage: [24] [120]-V ac, with integral control-power transformer, and overcurrent protection.

          - Enclosure: NEMA 250, [Type 1] [Type 3R] [Type 4] [Type 12] <Insert type> and [EEMAC-1].

          - Motor Overload Protection: Overload relay in each phase.

          - Starting Devices: Hand-off-automatic selector switch for each pump in cover of control panel, plus pilot device for automatic control.

            - Duplex, Automatic, Alternating Starter: Switches lead pump to lag main pump and to two-pump operation.

          - Liquid Gage Pressure Transmitter with Adjustable Span:

            - Performance:

              - Range: Minus 300 to 300 psig (Minus 2068 to 2068 kPa).

              - Span: Field adjustable.

              - Minimum Span: 3 psig (21 kPa).

              - Reference Accuracy: Within 0.07 percent of span or better.

              - Stability: Within 0.125 percent of upper range limit for 5 years.

              - Overpressure Limits: 3626 psig (25 000 kPa).

              - Process Temperature Limits: Minus 40 to 250 deg F (Minus 40 to 121 deg C).

              - Ambient Temperature Limits: Minus 40 to 185 deg F (Minus 40 to 85 deg C).

              - Temperature Effect: Within 0.025 percent of upper range limit plus 0.125 percent of span.

              - Shock and vibration shall not harm the transmitter.

            - Analog Output Current Signal:

              - Two-wire, 4- to 20-mA dc current source.

              - Signal capable of operating into 1000-ohm load.

              - Digital signal based on HART protocol carried with current signal.

              - Dampening: Field selectable from zero to 30 seconds.

            - Operator Interface: Zero and span adjustments located behind cover.

            - Construction:

              - Non-wetted parts of transmitter constructed of aluminum or stainless steel.

              - Enclosure with removable cover on each side.

              - Wetted parts of transmitter constructed of Type 316 stainless steel.

              - Threaded, NPS 1/4 (DN 8) process connection on bottom of instrument.

              - Drain/vent valve on process connection.

              - Two 1/2-inch (16-mm) trade size conduit connections on side of instrument enclosure.

              - Screw terminal block for wire connections.

              - NEMA 250, Type 4X.

              - Mounting Bracket: Appropriate for installation.

          - Pump Operation and Sequencing: [Pressure-sensing method] [or] [flow-sensing method] [Pressure-sensing method for lead pump and flow-sensing method for lag pumps].

            - Time Delay: Controls pump on-off operation; adjustable from [1 to 300] <Insert value> seconds.

            - The VFC's run the pumps to provide the lowest energy use or to meet the process parameters.  The optimization is accomplished through the pressure sensor

          - VFC: Voltage-source, pulse-width, modulating-frequency converter for [each] [lead] pump.

          - Manual Bypass: Magnetic contactor arranged to transfer to constant-speed operation upon VFC failure.

          - Instrumentation: Suction and discharge pressure gages.

          - Lights: Running light for each pump, and the following:

            - Walk.

            - Low pressure.

            - Overload.

            - Bypass Circuit.

          - Alarm Signal Device: Sounds alarm when backup pumps are operating.

            - Time Delay: Controls alarm operation; adjustable from [1 to 300] <Insert value> seconds, with [automatic] [manual] reset.

          - Thermal-bleed cutoff.

          - [Low-suction-pressure] cutout.

Optional features in four subparagraphs below are available. Revise to suit Project.

          - High-suction-pressure cutout.

          - Low-discharge-pressure cutout.

          - High-discharge-pressure cutout.

          - Direct Digital Control (DDC) System for HVAC: Provide auxiliary contacts for interface to [BACnet] [LonWorks] <Insert system> DDC system. DDC systems are specified in Section 230923 "Direct Digital Control (DDC) System for HVAC." Include the following:

            - On-off status of each pump.

            - Alarm status.

        - Base: Structural steel, painted with epoxy primer and blue final coat.

If Project has more than one pump package system, delete paragraph below and schedule systems on Drawings.

        - Capacities and Characteristics:

          - Minimum Pressure Rating: [150 psig (1035 kPa)] [250 psig (1725 kPa)] <Insert value>.

          - System Water Flow Rate: <Insert gpm (L/s)>.

          - Discharge Pressure: <Insert psig (kPa)>.

          - Header Size: <Insert NPS (DN)>.

          - Lead Pump:

            - Capacity: <Insert gpm (L/s)>.

            - Total Dynamic Head: <Insert feet (kPa)>.

            - Speed: <Insert rpm>.

            - Electrical Characteristics:

              - Motor Horsepower: <Insert value>.

              - Volts: [120] [240] [277] [380] [460] <Insert value>.

              - Phases: [Single] [Three].

              - Hertz: [60] [50].

          - Lag Pump:

            - Capacity: <Insert gpm (L/s)>.

            - Total Dynamic Head: <Insert feet (kPa)>.

            - Speed: <Insert rpm>.

            - Electrical Characteristics:

              - Motor Horsepower: <Insert value>.

              - Volts: [120] [240] [277] [380] [460] <Insert value>.

              - Phases: [Single] [Three].

              - Hertz: [60] [50].

          - Pump Package Electrical Characteristics:

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

        - Glycol Fill System – Optional:

          - Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; Series S-GLY or comparable product by the following:

            - <Insert manufacturer's name>.

          - Tank: Polyethylene tank with cover 53 gal (200 L).

            - Diameter: 22-inch (559 mm).

            - Height: 39-inches (990 mm).

          - Pump: 304 stainless steel rotary vane pump, close-coupled motor, and graphite bearings.

            - Motor Horsepower: 1/3-hp.

            - Volts: 120 V ac.

            - Phases: Single.

            - Hertz: 60.

            - Capacity: <Insert gpm (L/s)>

            - Pressure: <Insert psig (kPa)>.

          - Control Panel:

            - NEMA-1 or EEMAC-1 enclosure.

            - Main disconnect.

            - Low-level indicator light.

            - Low-level shut-off float.

            - Dry contact for remote low level alarm signal (5-A).

            - Three-position selector switch H-O-A.

          - Glycol Fill System Operation and Sequencing:

            - When the pressure switch has reached its set point, the pump is shut down.

            - Adjustable pressure relief valve, with discharge piped to tank.

            - Ball valves, pressure gages and silent bronze check valves are installed on the discharge of each pump.

            - A separate external relief valve to return the glycol solution to the holding tank.

            - In "Auto" mode, the low-level float installed in the tank shall disable the pump should the glycol level become dangerously low.

            - In "Manual" mode, the pump can serve to replenish the system with glycol. The low-level float does not disable the pump in "Manual" mode.

      - AUTOMATIC CONDENSATE PUMP UNITS

Units in this article are complete with pump, basin, and controls and have limited applications and small capacity.

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

          - Beckett Corporation.

          - Hartell Pumps; Milton Roy.

          - Little Giant Pump Co.

          - Mepco, LLC.

          - <Insert manufacturer's name>.

        - Description: Packaged units with corrosion-resistant pump, plastic tank with cover, and automatic controls. Include factory- or field-installed check valve and a 72-inch- (1800-mm-) minimum, electrical power cord with plug.

If Project has more than one type or configuration of automatic condensate pump unit, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Height to Inlet: <Insert inches (mm)>.

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: [120] <Insert value>.

            - Phase: Single.

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

- EXECUTION

      - EXAMINATION

        - Examine equipment foundations and anchor-bolt locations for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

Retain first two paragraphs below if required.

        - Examine roughing-in for piping systems to verify actual locations of piping connections before pump installation.

        - Examine foundations and inertia bases for suitable conditions where pumps are to be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PUMP INSTALLATION

In first paragraph below, retain "HI 1.4" option for centrifugal pumps and "HI 2.4" option for vertically mounted, turbine centrifugal pumps.

        - Comply with [HI 1.4] [and] [HI 2.4].

        - Install pumps to provide access for periodic maintenance including removing motors, impellers, couplings, and accessories.

        - Independently support pumps and piping so weight of piping is not supported by pumps and weight of pumps is not supported by piping.

        - Automatic Condensate Pump Units: Install units for collecting condensate and extend to open drain.

        - Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

          - Install base-mounted pumps on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below if vibration isolation is required. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

          - Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

          - Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

Retain "Equipment Mounting" Paragraph below for in-line pumps suspended from structure.

        - Equipment Mounting: Install in-line pumps with continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of size required to support weight of in-line pumps.

          - Comply with requirements for seismic-restraint devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

          - Comply with requirements for hangers and supports specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

      - ALIGNMENT

        - [Engage a factory-authorized service representative to perform] [Perform] alignment service.

Retain this article only for separately coupled, end- and double-suction centrifugal pumps.

        - Comply with requirements in Hydronics Institute standards for alignment of pump and motor shaft. Add shims to the motor feet and bolt motor to base frame. Do not use grout between motor feet and base frame.

        - Comply with pump and coupling manufacturers' written instructions.

        - After alignment is correct, tighten foundation bolts evenly but not too firmly. Completely fill baseplate with nonshrink, nonmetallic grout while metal blocks and shims or wedges are in place. After grout has cured, fully tighten foundation bolts.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with requirements for piping specified in Section 232213 "Steam and Condensate Heating Piping" and Section 232216 Steam and Condensate Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Where installing piping adjacent to pump, allow space for service and maintenance.

        - Connect piping to pumps. Install valves that are same size as piping connected to pumps.

        - Install suction and discharge pipe sizes equal to or greater than diameter of pump nozzles.

        - Install [check, shutoff, and throttling valves] [check valve and throttling valve with memory stop] [triple-duty valve] on discharge side of pumps.

        - Install [Y-type strainer] [suction diffuser] and shutoff valve on suction side of pumps.

        - Install flexible connectors on suction and discharge sides of base-mounted pumps between pump casing and valves.

        - Install pressure gages on pump suction and discharge or at integral pressure-gage tapping, or install single gage with multiple-input selector valve.

Retain first two paragraphs below for automatic condensate pump units.

        - Install check valve and gate or ball valve on each condensate pump unit discharge.

        - Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

        - Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

      - STARTUP SERVICE

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks according to manufacturer's written instructions.

          - Check piping connections for tightness.

          - Clean strainers on suction piping.

          - Perform the following startup checks for each pump before starting:

            - Verify bearing lubrication.

            - Verify that pump is free to rotate by hand and that pump for handling hot liquid is free to rotate with pump hot and cold. If pump is bound or drags, do not operate until cause of trouble is determined and corrected.

            - Verify that pump is rotating in the correct direction.

          - Prime pump by opening suction valves and closing drains, and prepare pump for operation.

          - Start motor.

          - Open discharge valve slowly.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain hydronic pumps.

END OF SECTION 232123