- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

  - Submittals

    - Product Data:

      - Submit dimensional drawings and technical data in conformance with client’s instructions.

      - Submit pump performance curve indicating point of operation.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

TYPICAL SPECIFICATION

Supply and install as shown on plans a Flo Fab Condensate System with ground level steel or cast iron tank Quadruplex system series Q-CVC-GV6-(___)-QP

Condensate system as designed and manufactured by FLO FAB.Pumps shall be mounted vertically and piped to the ground level receiver. The system shall be a factory manufactured one-piece assembly. It shall be an integrated unit with pumps,(select below) steel or cast iron receiver, level floats, thermometer, gauge glass, suction isolation butterfly valves, y strainers, and a quadruplex control panel and alternator. The control panel shall be furnished mounted on receiver & wired, or remote wall mounting. All necessary electrical controls and accessories assembled for a completely automatic operation.

Vertical-in-Line Circulation Pumps

    - Volute: cast iron threaded or flanged suction and discharge connections. Both end connections are 180° from each other.

    - Impeller: stamped brass or cast bronze, dynamically balanced, with a minimum clearance.

    - Shaft: stainless steel, fitted with bronze bushing and a butane rubber O-ring.

    - Sealing: Ceramic and carbon mechanical seal good to a working temperature of 135°C (275°F).

    - Motor: respecting the requirements of Section 15010.

    - Maximum Working Pressure: 862 kPa (125 psi).

    - Maximum Working Temperature: 107°C (225°F).

    - Size and Capacity: As specified on pump tables shown on plans and specifications.

    - Acceptable component: Flo Fab series GV6.

TANK (RECEIVER)

Receiver shall be _____ gallon 1/4” black steel or cast iron with 2” vent, ¾” drain and (2”or 3”) inlet connection.

Unit shall include two (2) or more level float assemblies for pump operation

Accessories included:

- ½” water gauge sight glass with stopcock.

- 2 5" Stem thermometer.

CONTROL PANEL

The Quadruplex control panel shall be Flo Fab series QP

QP  Panel includes the following:

- Nema 1 Enclosure

- Fusible main disconnect switch

- Magnetic starters with overload protection

- HOA selector switches

- 3rd leg overload protection

- Control transformer

- Power on light

- Pump running lights

- Motor overloads lights

- Electric alternator on multiple pumps

Options:

- .Wye type inlet strainer (2”or 3”).

- PART 3 – EXECUTION

  - General Installation

    - Mount pumps so that the fluid flows in the direction indicated by the arrow engraved on the body, that grease nipples are easily accessible and once power is applied to the motor that the impeller in rotating in the correct direction.

    - Install support elements or piping hangers such that the body of the pump does not support the any piping or equipment. Refer to details and installation instructions from the manufacturer.

    - Install a valve and piping between the drain connection on the pump volute and the floor drain.

    - Install a valve to be able to release entrapped air in the volute.

    - Install valves in conjunction with pressure gauges.

End of Section