- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Code of construction in Québec - Chapter 1 », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to :

      - ANSI / ASME B16.22, Wrought Copper and Copper-Alloy Solder Joint Pressure Fittings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

  - Submittals

    - Supply the required manuals and incorporate them into an « Instruction and Maintenance Manual ».

    - The maintenance manual will comprise of or indicate the following :

      - A description of the major components; the manufacturer, a type, series or model number reference, year constructed, horsepower rating, flow and pressure.

- PART 2 – PRODUCT

- Basis-of-Design Product: Subject to compliance with requirements, provide Flo Fab Inc; S-CVC,-D-CVC,-T-CVC,-Q-CVC or comparable product by the following:

  - CONDENSATE SYSTEM

- Supply and install as shown on plans a Flo Fab  CONDENSATE SYSTEM series CVC. The contractor shall furnish and install a Flo Fab Simplex, Duplex, Triplex, Quadruplex  automatic condensate unit, the pump shall deliver _____ GPM at _____ PSI at the pump.  Pump(s) shall be mounted vertically or horizontally and flanged to the receiver.  Pump(s) shall be bronze fitted centrifugal pump with 210oF mechanical seals coupled to _____ HP (single, three) phase (115, 208, 230, 460,575) volt, 60 Hertz, (1750, 3500) RPM, (open drip-proof, totally enclosed) electric motor. Isolation valve(s) shall provided between the pump(s) and the Tank. Inlet Basket strainer shall also be installed at the tank inlet.

A vent line shall be furnished from the pump seal chamber to the receiver.

- Pumps:

  - Type: [centrifugal condensate handling Flo Fab Select Series] <Insert pump designation> as defined in centrifugal pumps above

- Mounting: Horizontal or vertical type <Insert type>.

- Number of Pumps: [one] [Two] [Three] [four] <Insert Number>.

Pumps:

          - Type: [Separately coupled, vertically mounted, double-suction pump, Flo Fab Select Series] <Insert pump designation> as defined in centrifugal pump Articles above.

          - Mounting: [Vertical/Horizontal floor mounted] <Insert mounting>.

        - See Pump Shedule for details

        - Capacities and Characteristics:

          - Capacity: <Insert gpm (L/s)>.

          - Total Dynamic Head: <Insert feet (kPa)>.

          - Maximum Height to Inlet: <Insert inches (mm)>.

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

              - Motor Horsepower: <Insert value>.

              - Volts: [120] [240] [277] [380] [460] [575] <Insert value>.

              - Phases: [Single] [Three].

              - Hertz: [60] [50].

Select Required Tank <Insert size>.

      - A (15US gal) (cast iron or steel tank)

      - B (25US gal) (cast iron or steel tank)

      - C (35US gal) (cast iron or steel tank)

      - D (45US gal) (cast iron or steel tank)

      - E  (70US gal) (cast iron or steel tank)

      - F  (120US gal) (cast iron or steel tank)

        - Each control panel contains the following elements :

          - NEMA-1 (US) or EEMAC-1 (CANADA) enclosure;

          - Main disconnect;

          - Pilot light indicators ;

          - Low-level shut-off float;

          - 3 position selector switch «H-O-A»;

          - Dry contact for remote alarm signal

        - In ”Auto” mode, the low-level float installed in the tank shall disable the pump should the condensate level become dangerously low.

        - The low-level float does not disable the pump in « Manual » mode.

        - A vent line shall be furnished from the pump seal chamber to the receiver

        - Nema I UQK-2 float switch assembly

- PART 3 – EXECUTION

  - Installation

    - Power wiring, as required, shall be the responsibility of the electrical contractor.  All wiring shall be performed per manufacturer’s instruction and applicable state, federal, and local codes.

    - Control wiring for remote mounted switches and sensor / transmitters shall be the responsibility of the controls contractor. All wiring shall be performed per manufacturer’s instructions and applicable state, federal, and local codes.

    - Provide drains for bases and seals, piped to and discharging into floor drains.

    - Condensate System Operation and Sequencing:

    - When the level in the boiler(s) has reached its set point, the pump(s) will start..

    - In "Auto" mode, the low-level float installed in the tank shall disable the pump(s) should the condensate level become dangerously low.

End of Section