- PART 1 – GENERAL

  - References

    - All work shall be in conformance to the latest revision of « Building Code », unless otherwise indicated.

    - All work shall conform to the latest revised codes and standards that having jurisdiction, including but not limited to:

      - ANSI / ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

      - ANSI / ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

      - ANSI / ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

      - ANSI / ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

      - ANSI B18.2.1, Square and Hex Bolts and Screws.

      - ANSI / ASME B18.2.2, Square and Hex Nuts.

      - ANSI / AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

      - ASTM A47M, Specification for Ferritic Malleable Iron Castings.

      - ASTM A53, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

      - ASTM A536, Specification for Ductile Iron Castings.

      - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

      - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

      - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

      - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

  - Submittals

    - Product Data:

      - Submit dimensional drawings and technical data in conformance with client’s instructions.

      - Submit pump performance curve indicating point of operation.

  - Instruction and Maintenance Manual

    - Submit manufacturer’s installation and start-up instructions.

    - The maintenance manual will comprise of or indicate the following:

      - A description of the major components: the manufacturer’s series or model reference number, power rating, flow and pressure;

      - All details relating to the operation, care and maintenance of component;

      - A list of equivalent component replacements.

- PART 2 – PRODUCT

TYPICAL SPECIFICATION

Supply and install as shown on plans a Flo Fab Boiler Feed System with evelated steel tank Duplex system series S-BFCE-(____)-1000

Boiler Feed system as designed and manufactured by FLO FAB.Pumps shall be mounted horizontally and piped to the elevated receiver. The system shall be a factory manufactured one-piece assembly. It shall be an integrated unit with pumps,(select below) steel receiver,make-up valve,thermometer, gauge glass, suction isolation butterfly valves, y strainers, solenoid valve and a duplex control panel and alternator. The control panel shall be furnished mounted on receiver & wired, or remote wall mounting. All necessary electrical controls and accessories assembled for a completely automatic operation.

2.1 Horizontal Closed Coupled End Suction Pumps

    - Pumps are Flo Fab series 1000 are stand alone closed coupled pumps, single stage, with end suction volute that can be supported.  Servicing of the pump can be performed without disturbing the piping connections.

    - Volute: Cast Iron Class 30 (ASTM No. A 159) without foot support. Threaded connections for a pressure gauge at the discharge end, as well as for venting and draining. The volute will be provided with a replaceable wear ring.

    - Impeller: Cast Bronze (ASTM No. B 584), closed type, dynamically balanced, keyed to the stainless steel shaft and secured by a stainless steel bolt and washer.

    - Coupling: No coupling design, impeller is directly coupled to the motor shaft.

    - The wet-end components are sealed with a self-lubricating mechanical seal. The seal is composed of a ceramic seat, a rotating carbon ring, a viton bellow and all other materials in stainless steel. It is designed for continuous operation at maximum working temperature of 400°F (205°C) corresponding to a maximum working pressure of 1724 kPa (250 psi). A replaceable bronze sleeve installed on the pump shaft, to protect the shaft from undue wear by the mechanical seal.

    - Pumps designed for an operating pressure of [1200 kPa (175 psi)] [1724 kPa (250 psi)] [2068 kPa (300 psi)].

    - Motors: respecting the requirements of Section 15010, NEMA specifications, closed type, high efficiency, and foot mounted.

    - Selection of motor will allow the pump to operate at maximum capacity without surpassing the maximum amperage draw on the motor.

    - Each pump is hydrostatically tested.

    - Size and Capacity: As specified on pump tables shown on plans and specifications

    - Acceptable component: Flo Fab series 1000.

TANK (RECEIVER)

Receiver shall be _____ gallon 1/4” rolled black steel with 2” vent, ¾” drain     and (2”or 3”) inlet connection.

Unit shall include two (2) or more make-up valve assembly for pump operation

Accessories included:

- ½” water gauge sight glass with stopcock.

- 2 5" Stem thermometer.

- 3 make-up valve

CONTROL PANEL

The Duplex control panel shall be Flo Fab series SP

DP  Panel includes the following:

- Nema 1 Enclosure

- Fusible main disconnect switch

- Magnetic starters with overload protection

- HOA selector switches

- 3rd leg overload protection

- Control transformer

- Power on light

- Pump running lights

- Motor overloads lights

- Electric alternator on multiple pumps

Options:

- ·Receiver can be furnished in stainless steel or galvanized steel construction.

- .Receiver to be ASME code

- .¾” solenoid on larger units.

- .Wye type inlet strainer (2”or 3”).

- PART 3 – EXECUTION

  - General Installation

    - Mount pumps so that the fluid flows in the direction indicated by the arrow engraved on the body, that grease nipples are easily accessible and once power is applied to the motor that the impeller in rotating in the correct direction.

    - Install support elements or piping hangers such that the body of the pump does not support the any piping or equipment. Refer to details and installation instructions from the manufacturer.

    - Install a valve and piping between the drain connection on the pump volute and the floor drain.

    - Install a valve to be able to release entrapped air in the volute.

    - Install valves in conjunction with pressure gauges.

End of Section