TYPICAL SPECIFICATION

1.1. WORK INCLUDED

ACTION SUBMITTALS

        - Product Data: For each type of product indicated.

          - Include certified performance curves and rated capacities, operating characteristics, furnished specialties, electrical characteristics, and accessories for each type of product indicated.

          - Indicate pump's final impeller dimensions, and operating point on curves.

        - Shop Drawings: For each product indicated.  For pump packages include plans, elevations, sections, details, and attachments to other work.

          - Show pump layout, component layout and connections.

          - Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, model numbers, and location and size of each field connection.

          - Wiring Diagrams: For power, signal, and control wiring.

      - INFORMATIONAL SUBMITTALS

Retain "Performance Tests" paragraph below if retaining certification in "Quality Assurance" Article.

        - Performance Tests: For optional production performance tests in "Quality Assurance" Article.

        - Field Quality-Control Reports: Startup service reports.

        - Sample Warranty: For manufacturer's warranty.

      - CLOSEOUT SUBMITTALS

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Operation and Maintenance Data: For pumps to include in emergency, operation, and maintenance manuals.

          - Exploded view diagrams with component parts list.

          - Instructions for installation, start-up, and operation.

          - Description of maintenance and care procedures.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise "Mechanical seals", "Bearing sets" and "Couplings" Subparagraphs below to suit Project.

          - Mechanical seals: [One] <Insert number> mechanical seal(s) for each pump.

          - Bearing sets: [One] <Insert number> bearing set(s) for each pump.

          - Couplings: [One] <Insert number> coupling(s) for each pump.

      - QUALITY ASSURANCE

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain the following paragraph for optional acceptance tests by the manufacturer.  See the following website link for test details:

http://www.flofab.com/HomeSite/Literature/Documents/Certificates/Hydraulic%20Performance%20Tolerence/Brochure/en/?SessionNoClient=1347&SessionAdministrator=0

        - Production Performance Acceptance Tests:

          - ANSI/HI 14.6, Hydraulic Institute Performance Acceptance Tests: Five test points at levels 2B, 2U, or 3B.

          - Certified NPSH curve.

          - Factory witness test.

          - Certified motor test.

        - ASME Compliance:

          - ANSI/ASME B16.1, Cast Iron Pipe Flanges and Flanged Fittings, Class 25, 125, 250 and 800.

          - ANSI/ASME B16.3, Malleable-Iron Threaded Fittings, Classes 150 and 300.

          - ANSI/ASME B16.5, Pipe Flanges and Flanged Fittings, Steel Nickel Alloy and other Special Alloys.

          - ANSI/ASME B16.9, Factory-Made Wrought Steel Butt welding Fittings.

          - ANSI/ASME B18.2.1, Square and Hex Bolts and Screws.

          - ANSI/ASME B18.2.2, Square and Hex Nuts.

        - ASTM Compliance:

          - ASTM A47 / A47M, Specification for Ferritic Malleable Iron Castings.

          - ASTM A48 / A48M, Standard Specification for Gray Iron Castings.

          - ASTM A53 / A53M, Specification for Pipe, Steel, Black and Hot-Dipped, Zinc Coated, Welded and Seamless.

          - ASTM A536, Specification for Ductile Iron Castings.

          - ASTM B62, Specification for Composition Bronze or Ounce Metal Castings.

          - ASTM E202, Test Method for Analysis of Ethylene Glycols and Propylene Glycols.

        - AWWA Compliance:

          - ANSI/AWWA C111 / A21.11, Rubber Gasket Joints for Ductile-Iron and Gray-Iron Pressure Pipe and Fittings.

        - CSA Compliance:

          - CSA B242, Groove and Shoulder Type Mechanical Pipe Couplings.

          - CSA W47.1, Certification of Companies for Fusion Welding of Steel.

      - WARRANTY

Visit the website for a copy of the warranty and exclusions:

http://www.flofab.com/HomeSite/Literature/Documents/ARRA,%20Terms%20and%20conditions/Terms%20and%20Conditions/Brochure/en/Flo%20Fab%20Standard%20Terms%20and%20Conditions%20of%20Sale%20US%2011%20March,16.pdf

- Manufacturer's Warranty: Manufacturer undertakes during the period of warranty to
repair or to replace with new, in the shortest time possible, any parts found to present recognized defects in materials, construction or workmanship that render them unfit for the intended use.  The warranty on the products has the following duration from the date of shipping the material to job site:

          - Pumps: 5 years.

          - Packaged Systems: 8 years.

      - DELIVERY, STORAGE, AND HANDLING

        - Retain protective coatings and flange's protective covers during storage.

      - COORDINATION

        - Coordinate sizes and locations of concrete bases with actual equipment provided.

- PART 2 – PRODUCT

2.1. ACCEPTABLE MANUFACTURER

2.1.1.   The system shall be as manufactured by FLO FAB Incorporated, 860 Industriel Boulevard, Bois-des-Filion, Quebec, Canada, J6Z 4V7.

2.2. PRIMARY/SECONDAIRY SKID PACKAGE WITH BOILER(S)

      - LIQUID HANDLING with CENTRIFUGAL PUMPS

For pump selections, access the Flo Fab selection program with the following credentials: username is engineering and password is 8888.

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

        - Basis-of-Design Product: Subject to compliance with requirements, Designed, furnished and installed as shown on plans S-PS/B-D-PS/B-T-PS/B-Q-PS/B-P-PS/B simplex, duplex, triplex, quadruplex or pentraplex Flo Fab Inc primary/secondary with boiler(s) system; A single manufacturer regularly engaged in designing and manufacturing of heat transfer systems shall furnish the System.  Manufacturer shall provide technical assistance during installation and system start up. Product by the following: <Insert Number>.

        - Description: Factory-assembled and tested, centrifugal, overhung impeller, single-stage, pump(s) as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted vertically or horizontally.

1.2. SYSTEM DESCRIPTION

    - The system shall be a hydronic type consisting of cooper fin tube boiler(s),primary and secondary circulating pump(s), air separator, expansion tank, suction diffuser, check valve(s) balancing valve(s), pressure gauges and thermometer, service isolation valves, chemical pot feeder, glycol fill unit and control system. The system shall be designed for a performance capacity of _____________ TOTAL BTU/H output. Heat transfer package and control system shall be a factory pre-assembled on a structural steel frame and wired by FLO FAB Incorporated.

BOILER(S)

2.2.2.   The boiler(s) shall be a ______________model ______________ sized for a design output of ___________ BTU/hr and be _______% efficiency with 20ppm NOx or less.  Quantity of boilers:_____.

2.2.2.1    Heat source shall be natural gas or propane.

2.2.3.     Secondary Loop Supply Temperature: ___________ °F.

Secondary Loop Return Temperature: ___________ °F.

Secondary Loop System Volume: ___________ US gallons.

Secondary Loop System DP Required: ___________ psi.

Secondary Loop System Heat Load: ___________ BTU/hr.

PUMP(S) see schedule (select type of pump(s)

      - PUMP(S)

http://www.flofab.com/Main/Pumps/Pages/NewPumpSearch.aspx?action=Login&u=ENGINEERING&a=no&SessionNoClient=1347&SessionAdministrator=0

Use the following link for complete 3D, AutoCAD drawings, IOM, technical brochures, exploded view diagrams, parts list, and construction materials (select pump category and the applicable pump subcategory):

http://www.flofab.com/HomeSite/Literature/Pages/Literature#

The Flo Fab Model HC pump package consists of two (enter number) pumps, control panel with variable frequency controller (VFC), expansion tank, air separator, chemical bypass feeder, heat exchangers (shell and tube/plate), boilers, chillers, cooling towers, glycol fill system (optional), balancing valves, isolation valves, air vents, drains, multifunction valves, suction diffusers (or Y-pattern strainers), and interconnecting black steel schedule 40 piping.  All package components are mounted on a structural steel base with lifting lugs.  Assembly, testing, and final adjusting is performed at the factory.  The module will be onsite ready for mechanical and electrical system connections.

Edit centrifugal pump articles above and edit the "Pumps" paragraph below; first paragraph describes the vertically mounted, double suction pump used with the Model HC package.

          - Type: [Separately coupled, vertically mounted, double-suction pump, Flo Fab Select Series] <Insert pump designation> as defined in centrifugal pump Articles above.

          - Mounting: [Vertical/Horizontal floor mounted] <Insert mounting>.

          - Number of Pumps: [One] [Two] [Three] [Four] [Five]  <Insert Number>.

        - Capacities and Characteristics:

          - Minimum Pressure Rating: [150 psig (1035 kPa)] [250 psig (1725 kPa)] <Insert value>.

          - System Water Flow Rate: <Insert gpm (L/s)>.

          - Discharge Pressure: <Insert psig (kPa)>.

          - Header Size: <Insert NPS (DN)>.

          - Lead Pump:

            - Capacity: <Insert gpm (L/s)>.

            - Total Dynamic Head: <Insert feet (kPa)>.

            - Speed: <Insert rpm>.

            - Electrical Characteristics:

              - Motor Horsepower: <Insert value>.

              - Volts: [120] [240] [277] [380] [460] [575] <Insert value>.

              - Phases: [Single] [Three].

              - Hertz: [60] [50].

          - Lag Pump(s):

            - Capacity: <Insert gpm (L/s)>.

            - Total Dynamic Head: <Insert feet (kPa)>.

            - Speed: <Insert rpm>.

            - Electrical Characteristics:

              - Motor Horsepower: <Insert value>.

              - Volts: [120] [240] [277] [380] [460] [575]  <Insert value>.

              - Phases: [Single] [Three].

              - Hertz: [60] [50].

          - Pump Package Electrical Characteristics:

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

2.2.5.   EXPANSION TANK - See schedule for size and details:

The tank shall be installed vertically on the skid.  The tank must be connected to the system using a shut-off valve.

2.2.6.   AIR ELIMINATOR - See schedule for size and details:

The air separator shall be installed vertically on the skid.  The air separator shall be connected to the common suction header of the secondary loop pumps.

2.2.7.   BUTTERFLY VALVES

FLO FAB shall install stainless steel butterfly valves Series LBFVZ and shall be sized to minimize the pressure drop through the system.

2.2.8.   SILENT CHECK VALVES

FLO FAB shall install silent bronze check valves Series LSDDB on each secondary loop pump discharge.

2.2.9.   BALANCING VALVES

FLO FAB shall install globe style-balancing valves Series LGS on each secondary loop pump discharge. The valves shall be installed ten pipe size diameters after each pump discharge.

2.2.10.   SUCTION DIFFUSERS

FLO FAB shall install suction diffuser Series ASD on each secondary loop pump inlet. FLO FAB suction diffusers include a start-up and permanent strainer, and flow straightening vanes to avoid flow turbulence.

2.2.11.   PRESSURE GAUGES

FLO FAB shall install liquid filled pressure gauges with mini ball valves Series 2503 MxF on the common suction and discharge header of the secondary loop pumps.

2.2.12.   THERMOMETERS

FLO FAB shall install digital thermometers Series DVU with brass socket Series LE35 on the common suction and discharge header of the secondary loop pumps.

2.2.13.   ACCESSORIES

The common suction and discharge headers shall be of carbon steel. The end connection shall be grooved or flanged.  All welding of the frame and piping shall be performed by certified welders to ASME Section IX Code (Certificates provided upon request).

2.2.14.   CONTROL PANEL

The control panel shall be IEC type with overload relay(s) suitable for use at _____ volts, ____ phase, _____Hz, and shall be factory wired to the pump motor(s) and control system.  Magnetic starter(s) shall be included as a standard.  Fused disconnect switch(s) shall be provided with door interlock(s) to prevent opening electrical enclosure while system is energized.

The control panel shall be FLO FAB Series PSB to include the following:

(1)       CEMA 1 Enclosure

(1)       Fusible main disconnect switch

(1)       Magnetic starter with overload protection relay

(1)       Minimum run timer

(1)       HOA selector switch

(1)       Control transformer

(1)       Power on light

(1)       Pump running light

(1)       Motor overload light

Glycol Fill System

Basis-of-Design Product: Subject to compliance with requirements, provide

- Flo Fab Inc; S-GLY,-D-GLY,-T-GLY,-Q-GLY or comparable product by the following:

  - Glycol Fill System

The rotary vane positive displacement pump(s) series CYS shall be constructed 304 of stainless steel, and will have built-in By-Pass relief valve(s). The pump(s) shall have carbon graphite vanes, carbon rotating seal, ceramic stationary seal with Buna N bellows and stainless steel spring.

Pumps:

- Type: [Rotary vane glycol handling Flo Fab Select Series] <Insert pump designation> as defined in centrifugal pumps above

- Mounting: Horizontal type

- Number of Pumps: [one] [Two] [Three] [four] <Insert Number>.

    - Supply and install a device to pressurize a closed loop glycol system.

    - This device will automatically replenish the loss of glycol in a closed loop system. The device’s dimension are as follows:

Select Required Tank

      - A ECONO (53US gal) 22” (553 mm) x 39” (990 mm) (closed polyethylene tank with cover;

      - B  (25 US gal) 18” (457mm) x 28” (737mm closed polyethylene tank with cover;

      - C (53 US gal) 22” (559 mm) x 39” (990 mm) closed polyethylene tank with cover;

      - D (100 US gal) 30” (762 mm) x 43” (1092 mm) closed polyethylene tank with cover;

      - E (200 US gal) 30” (762 mm) x 87” (2210 mm)closed polyethylene tank with cover;

      - The pumping system contains the following elements:

      - See Pump schedule for details

        - Capacities and Characteristics

        - Motor: __ HP @ Volts: [120] [240] [208] [380] [460] [575] <.

        - Pump Capacity: ___ USGPM @ ________ head

        - Each control panel contains the following elements :

          - NEMA-1 (US) or EEMAC-1 (CANADA) enclosure;

          - Main disconnect;

          - Pilot light indicators ;

          - Low-level shut-off float;

          - System pressure switch;

          - 3 position selector switch «H-O-A»;

          - Dry contact for remote alarm signal.

        - When the pressure switch has reached its set point, the pump is shut down.

        - Adjustable pressure relief valve, with discharge piped to tank.

        - Ball valves, pressure gages and silent bronze check valves are installed on the discharge of each pump.

        - In ”Auto” mode, the low-level float installed in the tank shall disable the pump should the glycol level become dangerously low.

        - In « Manual » mode, the pump can serve to replenish the system with glycol. The low-level float does not disable the pump in « Manual » mode.

EXECUTION

Installation

Power wiring, as required, shall be the responsibility of the electrical contractor.  All wiring shall be performed per manufacturer’s instruction and applicable state, federal, and local codes.

Control wiring for remote mounted switches and sensor / transmitters shall be the responsibility of the controls contractor. All wiring shall be performed per manufacturer’s instructions and applicable state, federal, and local codes.

Provide drains for bases and seals, piped to and discharging into floor drains.

Glycol Fill System Operation and Sequencing:

When the pressure switch has reached its set point, the pump is shut down.

Adjustable pressure relief valve, with discharge piped to tank.

Ball valves, pressure gages and silent bronze check valves are installed on the discharge of each pump.

A separate external relief valve to return the glycol solution to the holding tank.

In "Auto" mode, the low-level float installed in the tank shall disable the pump should the glycol level become dangerously low.

In "Manual" mode, the pump can serve to replenish the system with glycol. The low-level float does not disable the pump in "Manual" mode.

2.2.16.   Digital electronic temperature control system shall be factory wired and programmed.  Temperature control system to include: supply temperature sensor, return temperature sensor, manual reset high limit with fault indicator light, status pilot lights and control circuit transformer.

2.2.17.   Primary/Secondary System operation shall be initiated by remote contact closure.  Once activated, the system shall monitor supply and return temperatures and stage the boiler(s) to maintain the desired temperature set point.  At the completion of the time cycle, the system shall reset to automatic mode.  System operation shall also be able to be initialized in automatic mode by remote contact closure. The system shall reset in automatic mode at the end of the cycle.

2.2.18.   Primary/Secondary System Operational Status outputs shall be provided for remote monitoring: freeze warning (where applicable), fluid temperature, high fluid temperature and system alarm.

2.2.19. Optional modem and service contract for remote monitoring of system shall be available.

PART 3. IMPLEMENTATION

3.1. TECHNICAL SERVICE

3.1.1. Submittal and installation drawings shall be as prepared by FLO FAB Incorporated and shall include scaled layout of heat transfer package, system schematic, electrical diagram, and other details.

3.2. INSTALLATION

3.2.1. PRIMARY/SECONDARY SKID PACKAGE

3.2.1.1. Pre-assembled Primary/secondary skid Package with boiler(s) shall be set in place by the project contractor.

3.2.1.2. Power wiring, remote sensor wiring and if subject to freezing, the required quantity of inhibited ethylene glycol ( Dowtherm SR-1) of propylene glycol ( Downfrost HD) shall be furnished by the project contractor.

3.2.1.3. Supply and return mains above grade or inside building shall be copper or schedule 40 black steel pipe, insulated, finished and installed by the project contractor.

- EXECUTION

      - EXAMINATION

        - Examine equipment foundations and anchor-bolt locations for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

Retain first two paragraphs below if required.

        - Examine roughing-in for piping systems to verify actual locations of piping connections before pump installation.

        - Examine foundations and inertia bases for suitable conditions where pumps are to be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PUMP INSTALLATION

In first paragraph below, retain "HI 1.4" option for centrifugal pumps and "HI 2.4" option for vertically mounted, turbine centrifugal pumps.

        - Comply with [HI 1.4] [and] [HI 2.4].

        - Install pumps to provide access for periodic maintenance including removing motors, impellers, couplings, and accessories.

        - Independently support pumps and piping so weight of piping is not supported by pumps and weight of pumps is not supported by piping.

        - Automatic Condensate Pump Units: Install units for collecting condensate and extend to open drain.

        - EQUIPMENT MOUNTING:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

          - Install base-mounted pumps on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below if vibration isolation is required. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

          - Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

          - Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

Retain "Equipment Mounting" Paragraph below for in-line pumps suspended from structure.

        - Equipment Mounting: Install in-line pumps with continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of size required to support weight of in-line pumps.

          - Comply with requirements for seismic-restraint devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

          - Comply with requirements for hangers and supports specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

      - ALIGNMENT

        - [Engage a factory-authorized service representative to perform] [Perform] alignment service.

Retain this article only for separately coupled, end- and double-suction centrifugal pumps.

        - Comply with requirements in Hydronics Institute standards for alignment of pump and motor shaft. Add shims to the motor feet and bolt motor to base frame. Do not use grout between motor feet and base frame.

        - Comply with pump and coupling manufacturers' written instructions.

        - After alignment is correct, tighten foundation bolts evenly but not too firmly. Completely fill baseplate with nonshrink, nonmetallic grout while metal blocks and shims or wedges are in place. After grout has cured, fully tighten foundation bolts.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with requirements for piping specified in Section 232213 "Steam and Condensate Heating Piping" and Section 232216 Steam and Condensate Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Where installing piping adjacent to pump, allow space for service and maintenance.

        - Connect piping to pumps. Install valves that are same size as piping connected to pumps.

        - Install suction and discharge pipe sizes equal to or greater than diameter of pump nozzles.

        - Install [check, shutoff, and throttling valves] [check valve and throttling valve with memory stop] [triple-duty valve] on discharge side of pumps.

        - Install [Y-type strainer] [suction diffuser] and shutoff valve on suction side of pumps.

        - Install flexible connectors on suction and discharge sides of base-mounted pumps between pump casing and valves.

        - Install pressure gages on pump suction and discharge or at integral pressure-gage tapping, or install single gage with multiple-input selector valve.

Retain first two paragraphs below for automatic condensate pump units.

        - Install check valve and gate or ball valve on each condensate pump unit discharge.

        - Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

        - Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

      - STARTUP SERVICE

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks according to manufacturer's written instructions.

          - Check piping connections for tightness.

          - Clean strainers on suction piping.

          - Perform the following startup checks for each pump before starting:

            - Verify bearing lubrication.

            - Verify that pump is free to rotate by hand and that pump for handling hot liquid is free to rotate with pump hot and cold. If pump is bound or drags, do not operate until cause of trouble is determined and corrected.

            - Verify that pump is rotating in the correct direction.

          - Prime pump by opening suction valves and closing drains, and prepare pump for operation.

          - Start motor.

          - Open discharge valve slowly.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain hydronic pumps.

END OF SECTION 232123